## CVR News
SCHEDULE
Name of the Work : Shifting of Overhead lines on 33KV Asifnagar 1 and Asifnagar 2 feeder emanating from 132KV Jubileehills and 11KV Appolo Feeder from 33/11KV Filmnagar SS at CVR News Channel, Film Nagar Signal, Jubleehills, Hyderabad replacing Existing OH Lines with underground cables for smooth passage of the vehicles and to provide free left at Film nagar signal on request of Zonal Commissioner, GHMC , Hyderabad.
WBS Element : G-2022-12-01-01-01-002
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.Number SSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 130 | Excavation & laying of UG Cable (Triple Run ) - Laying of XLPE UG cable Triple or more Run including excavation of trench of size 1000mm wide to 750mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever re quired depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates tobe adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs - Along the CC / BT multi layer road requiring compressor - 33 KV 3x400 Sqmm Cable. | Elect | Labour | SWR12019 | 1697.5 | M | 220675 | #VALUE!
2 | 60 | Excavation & laying of UG Cable (Triple Run )Laying of XLPE UG cable Triple or more Run including excavation of trench of size 1000mm wide to 750mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipeswherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates tobe adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. - Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR12024 | 1940 | M | 116400 | #VALUE!
3 | 30 | Hard Rock Cutting - Laying of 33kV XLPE UG Cable Triple run and above in Hard rock ( 1.2x0.75x1 = 0.9 cum) | Elect | Labour | SWR11800 | 2680 | M | 80400 | #VALUE!
4 | 440 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 200.1 | M | 88044 | #VALUE!
5 | 15 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR12004 | 317.5 | M | 4762.5 | #VALUE!
6 | 15 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) - 33KV 3x400 Sqmm Cable - Single Run | Elect | Labour | SWR11954 | 133 | M | 1995 | #VALUE!
7 | 6 | UG Cables Joints : Making of Straight through joints - 33kv 3x400 xlpe | Elect | Labour | SWR10382 | 5589 | EA | 33534 | #VALUE!
8 | 4 | Making of Outdoor/Indoor End Termination 33kv 3x400 xlpe | Elect | Labour | SWR10387 | 2710.55 | EA | 10842.2 | #VALUE!
9 | 280 | Supply of 6" B class GI pipe (5 mm thck 20 Kg/M) inlcuding cost of pipes and slabs | Elect | Supply | SMR40081 | 1044 | M | 292320 | #VALUE!
10 | 65 | Excavation & laying of UG Cable (Double Run) - Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs - Along the CC / BT multi layer road requiring compressor - 11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11981 | 1239.84 | M | 80589.6 | #VALUE!
11 | 60 | Excavation & laying of UG Cable (Double Run) Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs - Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) - 11 KV 3x300 Sqmm Cable | Elect | Labour | SWR11989 | 1420.65 | M | 85239 | #VALUE!
12 | 10 | Hard Rock Cutting - Laying of11KV XLPE UG cable Double Run of Size in Hard Rock(1.05*0.5x1=0.525cum) | Elect | Labour | SWR11004 | 1194 | RMT | 11940 | #VALUE!
13 | 25 | Raising of double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) - 11 KV 3x300 Sqmm Cable | Elect | Labour | SWR12005 | 270 | M | 6750 | #VALUE!
14 | 135 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 200.1 | M | 27013.5 | #VALUE!
15 | 2 | UG Cables Joints :Making of Straight through joints 11 KV 3x300 Sqmm Cable | Elect | Labour | SWR10386 | 3652.4 | EA | 7304.8 | #VALUE!
16 | 140 | Supply of 4" Bclass GI pipe 3.65mm thck 12.2kg/M | Elect | Supply | SMR40080 | 740 | M | 103600 | #VALUE!
17 | 1 | Erection of 11KV 400/200A Conventional type AB Switch including fixing of cross angles and alignment complete | Elect | Labour | SWR10393 | 2078 | EA | 2078 | #VALUE!
18 | 4 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4Mts.)duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1210 | EA | 4840 | #VALUE!
19 | 100 | Supply of GI Flat 25X3 mm with materials | Elect | Supply | SMR11485 | 105 | KG | 10500 | #VALUE!
20 | 5 | Supply of GI wire No 8 with materials | Elect | Supply | SMR11486 | 105 | KG | 525 | #VALUE!
21 | 40 | Supply of GI Bolts & Nuts, washers etc with materials | Elect | Supply | SMR11488 | 117.5 | KG | 4700 | #VALUE!
22 | 4 | Supply of CI eath pipe with 50mm dia,2.0 M Length | Elect | Supply | SMR11484 | 2441 | EA | 9764 | #VALUE!
23 | 1 | Supply of M+3 Tower (Galvanized) | Elect | Supply | SMR11683 | 140674.3 | EA | 140674.3 | #VALUE!
24 | 1 | Erection of M+3 Tower (Galvanized) | Elect | Labour | SWR11850 | 64576 | EA | 64576 | #VALUE!
25 | 1 | Supply of material for Extension of 3Mtrs for M+3 (Galvanized) | Elect | Supply | SMR11684 | 28520.64 | EA | 28520.64 | #VALUE!
26 | 1 | Erection of Extension of 3Mtrs for M+3 (Galvanized) | Elect | Labour | SWR11851 | 5067.6 | EA | 5067.6 | #VALUE!
27 | 1 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) (other than SS) - Drilling of Holes in Hard rock upto a depth of 3.3 Mtr hard rock blasting is not possible for 4 Nos. Tower legs | Elect | Labour | SWR30653 | 15015 | EA | 15015 | #VALUE!
28 | 1 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Box pole 9/10/11 Mtr | Elect | Labour | SWR11266 | 2591.99 | EA | 2591.99 | #VALUE!
29 | 1.04 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand, Cement and curing etc. -including the cost of cement. | Elect | Labour | SWR10356 | 6450 | M3 | 6708 | #VALUE!
30 | 1 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) (other than SS) - Drilling of Holes in Hard rock wherever rock blasting is not possible for pole/ RS joist Box pole/ 11 Mtr PSCC Pole/ 9 Mtr PSCC Pole/ | Elect | Labour | SWR30654 | 13750 | EA | 13750 | #VALUE!
31 | 2 | Formation of Cut point for 33 KV Double circuit line excludingpole erection and stays | Elect | Labour | SWR10466 | 3136 | EA | 6272 | #VALUE!
32 | 1 | Formation of Cut point for 11 KV Single Circuit line excluding pole erection and stays | Elect | Labour | SWR10653 | 1408.81 | EA | 1408.81 | #VALUE!
33 | 1 | Formation of Cut point for LT line excluding pole erection and stays for 3/4/5 wire | Elect | Labour | SWR21897 | 938 | EA | 938 | #VALUE!
34 | 2 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables(1C RO, 2C Al. Paint) | Elect | Labour | SWR10640 | 845 | EA | 1690 | #VALUE!
35 | 10 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 530 | #VALUE!
36 | 1 | Dismantling of Damaged Poles, not required and available in the middle of roads, transporting to stock point etc - Dism of 9.1M PSCC Pole | Elect | Labour | SWR11320 | 929.5 | EA | 929.5 | #VALUE!
37 | 3 | Dismantling of Damaged Poles, not required and available in the middle of roads, transporting to stock point etc - Dism of RS Joists 175 x 85 mm | Elect | Labour | SWR11324 | 736 | EA | 2208 | #VALUE!
38 | 1 | Dismantling of Damaged Poles, not required and available in the middle of roads, transporting to stock point etc - Dism of Box pole 9/10/11 Mtr | Elect | Labour | SWR11329 | 1130 | EA | 1130 | #VALUE!
39 | 0.085 | Dismantling of 11KV 34/55 sqmm SC | Elect | Labour | SWR22065 | 4419 | KM | 375.615 | #VALUE!
40 | 0.22 | Dismantling of 100 Sqmm Conductor DC. | Elect | Labour | SWR22064 | 11585 | KM | 2548.7 | #VALUE!
41 | 1 | Dismantling of M type tower | Elect | Labour | SWR11122 | 3484 | EA | 3484
42 | 3 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) - Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3235 | EA | 9705
43 | 0.8 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) - Upto 10 KM | Elect | Labour | SWR10131 | 333 | TO | 266.4
44 | 2 | LOADING of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 152
45 | 2 | UNLOADING of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 100
46 | 0.29 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 64.09
47 | 0.29 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 53.65
48 | 1 | LOADING of 11 KV AB SWCH Con 200/400 A | Elect | Labour | SWR10238 | 80 | EA | 80
49 | 1 | UNLOADING of 11 KV AB SWCH Con 200/400 A | Elect | Labour | SWR10556 | 80 | EA | 80
50 | 0.157 | LOADING of ACSR conductor scrap | Elect | Labour | SWR10257 | 491.02 | TO | 77.0901
51 | 0.157 | UNLOADING of ACSR conductor scrap | Elect | Labour | SWR10575 | 491.02 | TO | 77.0901
52 | 1.747 | LOADING of MS Scrap | Elect | Labour | SWR10258 | 578 | TO | 1009.766
53 | 1.747 | UNLOADING of MS Scrap | Elect | Labour | SWR10576 | 578 | TO | 1009.766
54 | 3 | Loading of 11/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 3072
55 | 3 | Unloading of 11/33KV XLPE UG Cable all sizes | Elect | Labour | SWR11231 | 1024 | DR | 3072
56 | 10 | Cutting charges for MS Sections - MS Channel 100 x 50 mm | Elect | Labour | SWR10294 | 10 | EA | 100
57 | 50 | Drilling of holes upto 20 mm dia using power drills - MS Channel, Angles and flat | Elect | Labour | SWR10307 | 4 | EA | 200
58 | 6 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 16470
59 | 220 | 11KV Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during latenight hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 6600
60 | 220 | 11KV Consultation charges for pursuing with various Departments for obtaining required permissions for Road cutting and submission of necessry Documents, Drawings etc. | Elect | Labour | SWR11801 | 37.5 | M | 8250
61 | 8 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters , CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 3872
62 | 15 | Supply of 31/2 XLPE 70sqmm LT cable | Elect | Supply | SMR40131 | 178.27 | M | 2674.05
63 | 15 | Laying of LT UG Cable - In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road - Lay-SR LT 3.5x70sqmm UG Cb HG/BC/CC/BT | Elect | Labour | SWR12363 | 275 | M | 4125
64 | 2 | Dimantle-Extension of M+3 Tower | Elect | Labour | SWR12480 | 2533.8 | EA | 5067.6
65 | 1.747 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) - Upto 10 KM | Elect | Labour | SWR10131 | 333 | TO | 581.751
66 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) - Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3235 | EA | 3235
67 | 2 | Providing of earthing with excavation of earth pit (0.6 x0.6x 2.4Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1210 | EA | 2420
68 | 2 | Earthing of Sub-Station - Supply of GI pipe 40 mm dia, 2 mtrs, 3mm thickness with bolts and nuts | Elect | Supply | SMR40091 | 733 | EA | 1466
69 | 0.015 | Restringing of existing loose Lines by removing the pin-binding and jumpers, Providing of temporary stays, providing stiffners pieces, replacement of damaged insulators, alignment of cross arms, pin binding and jumpering after tensioning and removing of the temporary stays complete 33/11 KV lines - Restringing of 100 Sqmm Single ckt 6 cond | Elect | Labour | SWR11311 | 12162.67 | KM | 182.4401
70 | 5 | Making of Outdoor/Indoor End Termination - 11 KV 3x300 Sqmm Cable | Elect | Labour | SWR10391 | 2324.15 | EA | 11620.75
| Sub Total: | [6 empty] | 1587918.1983 | 4835960.31 | 5995646.846
| 18% Service tax on labour | [6 empty] | 285825.2757 |  | 1641807.07
| Total Rs. | [6 empty] | 1873743.474 | 4835960.31 | 2962216.836

## Sandhya Hotels SS new (hidden)
SCHEDULE
Name of the Work : Erection of 33/11KV Indoor Substation with 2Nos. 12.5 MVA Power Transformers at SANDHYA HOTELS Opp Sunshine Hospitals Raidurgam under T&D Improvement Works.
WBS Element : S-1547-12-01-03-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 6 | Supply 9mtrs tubular poles single way | Elect | Labour | SMR40051 | 13913 | EA | 83478
2 | 6 | Errection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 8274
3 | 2 | SupCU Flexi jumper for Power T/F Neutral | Elect | Labour | SMR40033 | 4725 | EA | 9450
4 | 1 | LOADING of 50,63,75&100kva DTR | Elect | Labour | SWR10195 | 349.65 | EA | 349.65
5 | 1 | UNLOADING of 50,63,75&100kva DTR | Elect | Labour | SWR10513 | 280.35 | EA | 280.35
6 | 1 | Erection of Three Phase DTRs | Elect | Labour | SWR10463 | 1525 | EA | 1525
7 | 1 | Contruction of DTR column at 33/11kV SS | Elect | Labour | SWR23010 | 7235 | EA | 7235
8 | 1 | Erection of LT distribution box | Elect | Labour | SWR10674 | 1242 | EA | 1242
9 | 2600 | Laying contl cable10x2.5 Sqmm Cu cable | Elect | Labour | SWR11879 | 14 | M | 36400
10 | 1 | Supply of AC Supply panel complete | Elect | Labour | SMR40045 | 42000 | EA | 42000
11 | 1 | Erecction of AC/ DC control panel complete | Elect | Labour | SWR11893 | 2122 | EA | 2122
12 | 10 | LOADING of 33 KV VCBs&Panel boards | Elect | Labour | SWR10198 | 1024 | EA | 10240
13 | 10 | UN-LOADING of 33 KV VCBs&Panel boards | Elect | Labour | SWR10516 | 1024 | EA | 10240
14 | 10 | TRANSPORT OF COND DRUM,VCBs upto 10km | Elect | Labour | SWR11860 | 2667 | EA | 26670
15 | 10 | Erection of 33KV indoor switchgear panel | Elect | Labour | SWR10930 | 8990 | EA | 89900
16 | 750 | Supply,fabricati of 6mm Checkerd plates | Elect | Labour | SWR10873 | 83 | KG | 62250
17 | 12 | SupRubber mats( 6#x3#)size for indoorSS | Elect | Labour | SMR40068 | 1386 | EA | 16632
18 | 1 | Sup Alluminium Ladder for indoor works | Elect | Labour | SMR12378 | 1654 | EA | 1654
19 | 2 | Sup TrollyMounted Co2 Cylinders(IS-2878) | Elect | Labour | SMR40087 | 9240 | EA | 18480
20 | 2 | Sup Fire Buckets Stand with Buckets | Elect | Labour | SMR40088 | 1386 | SET | 2772
21 | 6 | Sup Fire Extinguisher for Control Room | Elect | Labour | SMR40089 | 4620 | EA | 27720
22 | 4 | Supply of Safety Helmet of standard make | Elect | Labour | SMR40071 | 231 | EA | 924
23 | 4 | Sup Earth Rods (8ft) Screw & clamp type | Elect | Labour | SMR40066 | 578 | EA | 2312
24 | 4 | Supply of Hand Gloves | Elect | Labour | SMR40067 | 289 | SET | 1156
25 | 1 | Sup Stand basic cell phone with charger | Elect | Labour | SMR40069 | 1386 | EA | 1386
26 | 1 | Sup Steel almarah(61/2 X 3ft) Godrej | Elect | Labour | SMR40061 | 9818 | EA | 9818
27 | 1 | Supply of Table (3x6ft) Godrej | Elect | Labour | SMR40057 | 6050 | EA | 6050
28 | 4 | Supply of S type chairs (Godrej) | Elect | Labour | SMR40058 | 924 | EA | 3696
29 | 1 | Sup Angle racks(18x36.6inches) Godrej | Elect | Labour | SMR40060 | 1733 | EA | 1733
30 | 10 | Supply of Danger boards with clamps | Elect | Labour | SMR40070 | 116 | EA | 1160
31 | 1 | Sup 33/11kv S.S Permanent name board | Elect | Labour | SMR40086 | 10238 | EA | 10238
32 | 1 | Supply of Wall clock standard make | Elect | Labour | SMR40059 | 578 | EA | 578
33 | 1 | SupTaparia Tool kit complete as per Spec | Elect | Labour | SMR40063 | 4925 | SET | 4925
34 | 2 | Sup Rechargeable LED torch light. | Elect | Labour | SMR40064 | 1733 | EA | 3466
35 | 1 | Supply of Hack saw (12 inches) | Elect | Labour | SMR40065 | 289 | EA | 289
36 | 8 | Supply of LC Boards | Elect | Labour | SMR40072 | 116 | EA | 928
37 | 2 | Supply of Gum Boots | Elect | Labour | SMR40073 | 693 | EA | 1386
38 | 1 | Supply of Digital clamp meter. | Elect | Labour | SMR40076 | 2888 | EA | 2888
39 | 1 | Supply of 5000v megger | Elect | Supply | SMR40074 | 13860 | EA | 13860
40 | 1 | Sup &fix of board ind Switchyard layout | Elect | Labour | SWR20032 | 1654 | EA | 1654
41 | 1 | Sup& fix safety inst/SS Op. inst board | Elect | Supply | SWR22090 | 2205 | EA | 2205
42 | 6 | Supply of 150 W LED Fixture set | Elect | Labour | SMR23116 | 13500 | EA | 81000
43 | 36 | Supply of CI pipe of 100 mm dia 2.75 mtr | Elect | Labour | SMR11482 | 3486 | EA | 125496
44 | 2 | Supply of GI pipe of 40 mm dia 2 mtrs | Elect | Labour | SMR11480 | 698 | EA | 1396
45 | 8.8 | Earth work excav for founda lead&lifts | Elect | Supply | SWR10857 | 331 | M3 | 2912.8
46 | 90 | Laying of LT 185 S.Run AR in HG/NS/CC/BT | Elect | Labour | SWR11923 | 295 | M | 26550
47 | 10 | Raising of UG Cable LT 3 1/2 x 185 Sqmm | Elect | Supply | SWR11959 | 67 | M | 670
48 | 2 | sup of LT3.5x185sqmm od/id termination k | Elect | Labour | SMR40140 | 550 | EA | 1100
49 | 2 | OD/Idoor end termination LT 3 1/2 x 185 | Elect | Supply | SWR10765 | 809 | EA | 1618
50 | 50 | Laying of 11kV35 S.Run AR in HG/NS/CC/BT | Elect | Labour | SWR11922 | 339 | M | 16950
51 | 15 | Raising of UG Cable 11 KV 3x35 Sqmm 3 | Elect | Supply | SWR11958 | 87 | M | 1305
52 | 2 | OD/Idoor end termination 11kv 3x35 xlpe | Elect | Supply | SWR10388 | 1444 | EA | 2888
53 | 2 | Erection of RS Joist 150 x 150 mm | Elect | Supply | SWR10348 | 1407 | EA | 2814
54 | 4 | Erection of RS Joist 175 x 85 mm | Elect | Supply | SWR10346 | 1131.9 | EA | 4527.6
55 | 638.29 | Laying of earth mat,excavation 75x 8mm | Elect | Supply | SWR10920 | 65 | RMT | 41488.85
56 | 250 | Laying of Earth mat 50x6mm flat | Elect | Supply | SWR21170 | 65 | M | 16250
57 | 16 | LOADING of 11 KV VCBs&Panel boards | Elect | Supply | SWR10199 | 1024 | EA | 16384
58 | 16 | UNLOADING of 11 KV VCBs&Panel boards | Elect | Supply | SWR10517 | 1024 | EA | 16384
59 | 16 | Erection of 11KV indoor switchgear panel | Elect | Supply | SWR10931 | 7980 | EA | 127680
60 | 1 | LOADING of 11 KV AB SWCH T.T.200/400 A | Elect | Supply | SWR10238 | 80 | EA | 80
61 | 1 | UNLOADING of 11 KV AB SWCH T.T.200/400 A | Elect | Supply | SWR10556 | 80 | EA | 80
62 | 1 | Erection of 11kv ABSwitch incl earthing | Elect | Supply | SWR10393 | 1598.34 | EA | 1598.34
63 | 1 | LOADING of 11 KV HG Fuse Sets | Elect | Supply | SWR10231 | 18 | EA | 18
64 | 1 | UNLOADING of 11 KV HG Fuse Sets | Elect | Supply | SWR10549 | 18 | EA | 18
65 | 1 | Erect. of 11kv HG Fuseset incl earthing | Elect | Supply | SWR10395 | 660 | SET | 660
66 | 500 | Cable terminations to the switchgear | Elect | Supply | SWR20813 | 27 | LS | 13500
67 | 1 | Loading 220 V Battery with Charger | Elect | Supply | SWR11166 | 1612 | SET | 1612
68 | 1 | Un-loading 220 V Battery with Charger | Elect | Supply | SWR11147 | 1024 | SET | 1024
69 | 1 | Erec 220V Battery with charger incl eart | Elect | Supply | SWR11772 | 5053 | EA | 5053
70 | 2 | Fab & laying of ladder in cable trench | Elect | Supply | SWR22088 | 788 | EA | 1576
71 | 6 | Fixing of LED/Metal halide complete. | Elect | Supply | SWR10956 | 1268 | EA | 7608
72 | 3.35 | Sup Material for 1st coat Al. Painting. | Elect | Supply | SMR40009 | 2181 | TO | 7306.35
73 | 9 | Painting suppports of 0.3m with bitumen | Elect | Supply | SWR10880 | 688 | EA | 6192
74 | 1 | Painting AB switch OP rods with PO red | Elect | Supply | SWR10881 | 142 | EA | 142
75 | 2 | Transport of 12.5MVA power transformer | Elect | Supply | SWR10855 | 27431 | EA | 54862
76 | 2 | LOADING of 12.5 MVA PTR | Elect | Supply | SWR10614 | 12128 | EA | 24256
77 | 2 | UNLOADING of 12.5 MVA PTR | Elect | Supply | SWR10628 | 12128 | EA | 24256
78 | 2 | Erection of 12.5 MVA PTR. | Elect | Labour | SWR10929 | 51818 | EA | 103636
79 | 36 | Errection of CI Earth pit as per IS3043 | Elect | Labour | SWR10923 | 2122 | EA | 76392
80 | 2 | Provd earthing with pit incl. GI pipe | Elect | Supply | SWR20182 | 1048 | EA | 2096
81 | 16 | TRANSPORT OF COND DRUM,VCBs upto 10km | Elect | Labour | SWR11860 | 2667 | EA | 42672
82 | 3.35 | Fabrication of struc.with power drilling | Elect | Labour | SWR10868 | 6852 | TO | 22954.2
83 | 9 | Fabrication of 175x85/150x75mm RS joist | Elect | Supply | SWR10642 | 402 | EA | 3618
84 | 12 | Fixing of 90lb rail poles for T/F | Elect | Labour | SWR11008 | 403 | RMT | 4836
85 | 3.35 | Sup Material for 2nd coat Al. Painting. | Elect | Labour | SMR40010 | 1293 | TO | 4331.55
86 | 3.35 | Labour for 1st coat Al. Painting. | Elect | Labour | SWR10877 | 851 | TO | 2850.85
87 | 3.35 | Labour for 2nd coat Al. Painting. | Elect | Labour | SWR10879 | 482 | TO | 1614.7
88 | 22 | Line//Load-33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 22528
89 | 22 | Unload-33KV XLPE UG Cable all sizes | Elect | Labour | SWR11231 | 1024 | DR | 22528
90 | 11 | TRANSPORT OF COND DRUM,VCBs upto 10km | Elect | Labour | SWR11860 | 2667 | EA | 29337
91 | 400 | Laying of 33kV 6 Run in AR in CC/BT cmp.cuttng | Elect | Labour | SWR12069 | 1815 | M | 726000
92 | 430 | Laying of 33kV 5 Run in HG | Elect | Labour | SWR12053 | 1045 | M | 449350
93 | 200 | Laying of 33kV 5 Run in Xing in CC/BT cmp.cuttng | Elect | Labour | SWR12061 | 1870 | M | 374000
94 | 820 | Laying of 33kV 5 Run in AR in CC/BT cmp.cuttng | Elect | Labour | SWR12057 | 1705 | M | 1398100
95 | 1000 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 91 | M | 91000
96 | 300 | Laying 33kV D.Run Xing in CC/BT cmp.cuttng | Elect | Labour | SWR11988 | 1240 | M | 372000
97 | 1560 | Laying 33kV D.Run AR in CC/BT cmp.cuttng | Elect | Labour | SWR11980 | 1085 | M | 1692600
98 | 400 | Laying 33kV D.Run HG | Elect | Labour | SWR11972 | 585 | M | 234000
99 | 290 | Laying 33kV D.Run Hard Rock | Elect | Labour | SWR11002 | 1430 | RMT | 414700
100 | 2690 | Laying of 2nd cable in excavated trench | Elect | Supply | SWR10988 | 91 | M | 244790
101 | 70 | Laying 33kV 3.Run xing in CC/BT cmp.cuttng | Elect | Supply | SWR12024 | 1552 | M | 108640
102 | 70 | Laying of 2nd cable in excavated trench | Elect | Supply | SWR10988 | 91 | M | 6370
103 | 305 | Raising of 33 KV 3x400 Sqmm Cable on support | Elect | Labour | SWR12004 | 254 | M | 77470
104 | 16 | Outdoor end termination 33kv 3x400 xlpe | Elect | Labour | SWR10387 | 2310 | EA | 36960
105 | 4 | Indoor end termination 33kv 3x400 xlpe | Elect | Labour | SWR10387 | 2310 | EA | 9240
106 | 40 | Straight through joint 33kv 3x400 xlpe | Elect | Labour | SWR10382 | 4764 | EA | 190560
107 | 400 | Supply of 250 mm Hume pipe of class NP3 | Elect | Labour | SMR40077 | 363 | M | 145200
108 | 1000 | Supply of 6" B class GI pipe | Elect | Labour | SMR40081 | 1044 | M | 1044000
109 | 200 | Supply of 6" DWC pipe | Elect | Labour | SMR11610 | 1012 | M | 202400
110 | 4 | LOADING of 33 KV AB SWCH Con 400/800 A | Elect | Labour | SWR10239 | 126 | EA | 504
111 | 4 | UNLOADING of 33 KV AB SWCH Con 400/800 A | Elect | Labour | SWR10557 | 79 | EA | 316
112 | 4 | Erection of 33kv ABSwitch incl earthing | Elect | Labour | SWR10392 | 2048.16 | EA | 8192.64
113 | 9 | Erection of Box Pole | Elect | Labour | SWR11266 | 2048 | EA | 18432
114 | 18 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1368
115 | 18 | Unloading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 900
116 | 18 | Coping&muffing of iron poles | Elect | Labour | SWR11890 | 3893 | M3 | 70074
117 | 18 | Painting of RS Joist(1C RO, 2C Al.Paint) | Elect | Labour | SWR10640 | 951 | EA | 17118
118 | 18 | Fabrication of 175x85/150x75mm RS joist | Elect | Labour | SWR10642 | 402 | EA | 7236
119 | 7.92 | PCC 1:3:6 using 40mm metal | Elect | Labour | SWR33029 | 5363 | M3 | 42474.96
120 | 7.92 | Earth work excav for founda lead&lifts | Elect | Labour | SWR10857 | 331 | M3 | 2621.52
121 | 60 | Laying of earth mat,excavation 25x3mm | Elect | Labour | SWR10921 | 68 | RMT | 4080
122 | 4 | Coil earthing of pole with No.8 GI wire | Elect | Labour | SWR22091 | 386 | EA | 1544
123 | 4 | Supply of CI pipe of 100 mm dia 2.75 mtr | Elect | Supply | SMR11482 | 3486 | EA | 13944
124 | 4 | Errection of CI Earth pit as per IS3043 | Elect | Supply | SWR10923 | 2122 | EA | 8488
125 | 1 | TRANSPORT OF COND DRUM,VCBs upto 10km | Elect | Supply | SWR11860 | 2667 | EA | 2667
126 | 0.8 | Stringing 100sqmm 33/11kv Line 3 Cond SC | Elect | Labour | SWR10366 | 13585 | KM | 10868
127 | 5 | Horizontal Cut point for 33 KV line | Elect | Labour | SWR10981 | 1756 | EA | 8780
128 | 1 | LOADING of Conductor drums | Elect | Labour | SWR10191 | 202 | EA | 202
129 | 1 | UNLOADING of Conductor drums | Elect | Labour | SWR10509 | 97 | EA | 97
130 | 57 | LOADING of 33 KV Pin insulators | Elect | Labour | SWR10211 | 2.73 | CRT | 155.61
131 | 57 | UNLOADING of 33 KV Pin insulators | Elect | Labour | SWR10529 | 2.73 | CRT | 155.61
132 | 1 | LOADING of 33KV Metal parts-bag of 25no | Elect | Labour | SWR10618 | 65 | BAG | 65
133 | 1 | UNLOADING of 33 KV Metal parts-bagof 25 | Elect | Labour | SWR10632 | 65 | BAG | 65
134 | 20 | Erection of Spun poles 12.5 Mtrs | Elect | Labour | SWR10350 | 4433 | EA | 88660
135 | 20 | Transport of 12.5 Mtrs Spun poles | Elect | Labour | SWR11181 | 858 | EA | 17160
136 | 20 | LOADING of Spun poles 12.5 Mtrs | Elect | Labour | SWR10190 | 548 | EA | 10960
137 | 20 | UNLOADING of Spun poles 12.5 Mtrs | Elect | Labour | SWR10508 | 363 | EA | 7260
138 | 60 | Fabrication of Back clamps with 75 x 8 mm MS Flat . | Elect | Labour | SWR10319 | 31 | EA | 1860
139 | 60 | Fab V.Cross arms with 100x50 mm MS Channel 33Kv | Elect | Labour | SWR10312 | 152 | EA | 9120
140 | 30 | Earth work excav for founda lead&lifts | Elect | Labour | SWR10857 | 331 | M3 | 9930
141 | 2 | S-M+3 Tower Galv | Elect | Labour | SMR11683 | 127700 | EA | 255400
142 | 2 | Erect M+3 Tower Galv | Elect | Labour | SWR11850 | 63309 | EA | 126618
143 | 9.5 | Excvt Pit Hard w/o Blst 1.2mX1.2MX3.3M | Elect | Labour | SWR12090 | 5189 | EA | 49295.5
144 | 29 | Line2\\Load-11KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 29696
145 | 29 | Unload-11KV XLPE UG Cable all sizes | Elect | Labour | SWR11231 | 1024 | DR | 29696
146 | 15 | TRANSPORT OF COND DRUM,VCBs upto 10km | Elect | Labour | SWR11860 | 2667 | EA | 40005
147 | 450 | Laying 11kV 300 S.Run AR in CC/BT cm.ctg | Elect | Supply | SWR11928 | 839 | M | 377550
148 | 50 | Laying 11kV 300Xing S.Rn CC/BT comp.cutt | Elect | Labour | SWR11937 | 937 | M | 46850
149 | 100 | Laying 11KV300 S.Run AR in HG | Elect | Labour | SWR11919 | 363 | M | 36300
150 | 400 | Laying 11kV 300D.Run AR in CC/BT cmp.cut | Elect | Supply | SWR11981 | 988 | M | 395200
151 | 100 | Laying of 11kV UG 2Run in Hard rock. | Elect | Labour | SWR11004 | 1194 | RMT | 119400
152 | 150 | Layin11KV300sqmm D.Run AR in HG | Elect | Labour | SWR11973 | 493 | M | 73950
153 | 650 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 91 | M | 59150
154 | 50 | Laying 11KV300 3Run AR in HG | Elect | Labour | SWR12014 | 612 | M | 30600
155 | 200 | Laying 11kV 300 3.Run AR in CC/BT cm.ctg | Elect | Supply | SWR12020 | 1238 | M | 247600 | 201
156 | 70 | Laying 11kV 300 3.Run XING in CC/BT cm.ctg | Elect | Labour | SWR12025 | 1416 | M | 99120
157 | 640 | Laying of 2nd cable in excavated trench | Elect | Supply | SWR10988 | 91 | M | 58240
158 | 150 | Laying 11kV 300 6.Run AR in CC/BT cm.ctg | Elect | Labour | SWR12070 | 1705 | M | 255750
159 | 100 | Laying 11KV300 6Run in HG | Elect | Supply | SWR12066 | 990 | M | 99000
160 | 1250 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 91 | M | 113750
161 | 70 | Laying of 2nd cable in excavated trench ( 1 Run in 33KV 3Runs Trench ) | Elect | Labour | SWR10988 | 91 | M | 6370
162 | 4800 | Laying of 2nd cable in excavated trench(4 Run in 33KV 5Run Trench) | Elect | Supply | SWR10988 | 91 | M | 436800
163 | 2000 | Laying of 2nd cable in excavated trench(5 Run in 33KV 6Run Trench) | Elect | Labour | SWR10988 | 91 | M | 182000
164 | 270 | Raising of UG Cable 11 KV 3x300 Sqmm | Elect | Labour | SWR11955 | 113 | M | 30510
165 | 20 | OD/Idoor end termination 11kv 3x300 xlpe | Elect | Labour | SWR10391 | 2021 | EA | 40420
166 | 50 | Straight through joint 11kv 3x300 xlpe | Elect | Labour | SWR10386 | 3176 | EA | 158800
167 | 300 | Supply of 150 mm Hume pipe of class NP3 | Elect | Labour | SMR40078 | 303 | M | 90900
168 | 900 | Supply of 4" B class GI pipe | Elect | Labour | SMR40080 | 740 | M | 666000
169 | 600 | Supply of 4" DWC pipe | Elect | Labour | SMR11609 | 759 | M | 455400
170 | 5400 | Consult charg for providng traffic diver | Elect | Labour | SWR21903 | 30 | M | 162000
171 | 5400 | Consultation charges for pursuing with v | Elect | Labour | SWR11801 | 30 | M | 162000
172 | 8 | LOADING of 11 KV AB SWCH Con 200/400 A | Elect | Labour | SWR10238 | 80 | EA | 640
173 | 8 | UNLOADING of 11 KV AB SWCH Con 200/400 A | Elect | Labour | SWR10556 | 80 | EA | 640
174 | 8 | Coil earthing of pole with No.8 GI wire | Elect | Labour | SWR22091 | 386 | EA | 3088
175 | 8 | Supply of CI pipe of 100 mm dia 2.75 mtr | Elect | Labour | SMR11482 | 3486 | EA | 27888
176 | 8 | Errection of CI Earth pit as per IS3043 | Elect | Labour | SWR10923 | 2122 | EA | 16976
177 | 8 | Erection of 11kv ABSwitch incl earthing | Elect | Labour | SWR10393 | 1598.34 | EA | 12786.72
178 | 7.04 | PCC 1:3:6 using 40mm metal | Elect | Labour | SWR33029 | 5363 | M3 | 37755.52
179 | 7.04 | Earth work excav for founda lead&lifts | Elect | Supply | SWR10857 | 331 | M3 | 2330.24
180 | 8 | Fabrication of 175x85/150x75mm RS joist | Elect | Labour | SWR10642 | 402 | EA | 3216
181 | 8 | Erection of Box Pole | Elect | Labour | SWR11266 | 2048 | EA | 16384
182 | 16 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1216
183 | 16 | Unloading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 800
184 | 16 | Coping&muffing of iron poles | Elect | Labour | SWR11890 | 3893 | M3 | 62288
185 | 16 | Painting of RS Joist(1C RO, 2C Al.Paint) | Elect | Supply | SWR10640 | 951 | EA | 15216
186 | 1 | TRANSPORT OF COND DRUM,VCBs upto 10km | Elect | Supply | SWR11860 | 2667 | EA | 2667
187 | 100 | Laying of earth mat,excavation 25x3mm | Elect | Supply | SWR10921 | 68 | RMT | 6800
188 | 18 | LOADING of 11 KV - Cross arms | Elect | Supply | SWR10228 | 3 | EA | 54
189 | 18 | UNLOADING of 11 KV Cross arms | Elect | Supply | SWR10546 | 3 | EA | 54
190 | 6 | Cut point for 11 KV line | Elect | Supply | SWR10653 | 1119 | EA | 6714
191 | 0.7 | Stringing of 55 Sqmm Single Circuit (3 Conductors) | Elect | Supply | SWR10365 | 7469 | KM | 5228.3
192 | 8.8 | Earth work excav for founda lead&lifts 11KV | Elect | Labour | SWR10857 | 331 | M3 | 2912.8
193 | 42 | LOADING of 11 KV Pin insulators | Elect | Labour | SWR10212 | 1.05 | CRT | 44.1
194 | 42 | UNLOADING of 11 KV Pin insulators | Elect | Supply | SWR10530 | 1.05 | CRT | 44.1
195 | 24 | LOADING of 11 KV Disc insulators | Elect | Labour | SWR12416 | 1.84 | CRT | 44.16
196 | 24 | UNLOADING of 11 KV Disc insulators | Elect | Supply | SWR10631 | 1.84 | CRT | 44.16
197 | 1 | LOADING of 11KV Metal parts-bag of 50no | Elect | Labour | SWR12402 | 48 | BAG | 48
198 | 1 | UNLOADING of 11 KV Metal parts-bagof 50 | Elect | Labour | SWR12421 | 48 | BAG | 48
199 | 38 | Fabrication of Back clamps with 75 x 8 mm MS Flat | Elect | Labour | SWR10319 | 31 | EA | 1178
200 | 30 | Fab V.Cross arms with 100x50 mm MS Channel 11Kv | Elect | Labour | SWR10312 | 152 | EA | 4560
201 | 10 | Erection of 9.1 Pscc Poles | Elect | Labour | SWR10343 | 1621 | EA | 16210
202 | 6 | Erection of Strut pole 9.1pscc pole | Elect | Labour | SWR11083 | 1621 | EA | 9726
| Sub Total: | [6 empty] | 14880866.18
| 18% Service tax on labour | [6 empty] | 2678555.9124
| Total Rs. | [6 empty] | 17559422.0924

## ADITYA EMPRESS TOWERS (hidden)
SCHEDULE
Name of the Work : Erection of 33/11KV Indoor Substation with 2Nos. 12.5 MVA Power Transformers at SANDHYA HOTELS Opp Sunshine Hospitals Raidurgam under T&D Improvement Works.
WBS Element : S-1547-12-01-03-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 1 | Erection of Three Phase DTRs | Elect | Labour | SWR10463 | 1524 | EA | 1524
2 | 1 | LOADING of 15&25kva DTR | Elect | Labour | SWR10194 | 135 | EA | 135
3 | 1 | UNLOADING of 15&25kva DTR | Elect | Labour | SWR10512 | 135 | EA | 135
4 | 1 | Construction of DTR column for 33/11kV Sub-station as per the DATA-XI | Elect | Labour | SWR22055 | 28861 | EA | 28861
5 | 1 | Erection of 11 KV HG Fuse set including earthing | Elect | Labour | SWR10395 | 660 | SET | 660
6 | 1 | LOADING of 11 KV HG Fuse Sets | Elect | Labour | SWR10231 | 18 | EA | 18
7 | 1 | UNLOADING of 11 KV HG Fuse Sets | Elect | Labour | SWR10549 | 18 | EA | 18
8 | 1 | Erection of 11 KVAB Switch 400/200 A conventional type including alignment and earthing | Elect | Labour | SWR10393 | 1641 | EA | 1641
9 | 1 | LOADING of 11 KV AB Switch Tilting type | Elect | Labour | SWR10237 | 82 | SET | 82
10 | 1 | UNLOADING of 11 KV AB Switch Tilting type | Elect | Labour | SWR10555 | 82 | SET | 82
11 | 1 | Erection of LT distribution box including laying of LT cable from distribution box to LT OH line and DTR to distribution box including earthing of distribution box and crimping of lugs connecting of jumpers etc (Excluding material) | Elect | Labour | SWR10674 | 1242 | EA | 1242
12 | 90 | Laying of In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road-LT 3 1/2 x 185/120/95/70/50 Sqmm Cable in Single Run | Elect | Labour | SWR10433 | 295 | M | 26550
13 | 10 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) -LT 3 1/2 x 185/120/95/70/50 Sqmm Cable | Elect | Labour | SWR10452 | 67 | M | 670
14 | 2 | Making of Outdoor/Indoor end termination LT 3 1/2 x 185 | Elect | Labour | SWR10765 | 809 | EA | 1618
15 | 50 | Excavation & laying of UG Cable in Single Run,In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil / CC/BT Road,11 KV 3x35 Sqmm Cable | Elect | Labour | SWR20855 | 339 | M | 16950
16 | 15 | Raising of UG Cable 11 KV 3x35 Sqmm 3 | Elect | Labour | SWR10451 | 87 | M | 1305
17 | 1 | Making of Outdoor/Indoor End Termination,11 KV 3x35 Sqmm Cable | Elect | Labour | SWR10388 | 1444 | EA | 1444
18 | 7.5 | Fabrication of Main and Auxiliary structures with welding using raw steel such as RS joist, M.S.Angles, Plates, Channels, including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3597 | TO | 26977.5
19 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) | Elect | Labour | SWR10139 | 2667 | KM | 2667
20 | 2 | Erection of 12.5 MVA PTR. | Elect | Labour | SWR10929 | 51818 | EA | 103636
21 | 2 | Transport of 12.5MVA power transformer | Elect | Labour | SWR10855 | 27431 | EA | 54862
22 | 2 | LOADING of 12.5 MVA PTR | Elect | Labour | SWR10614 | 12128 | EA | 24256
23 | 2 | UNLOADING of 12.5 MVA PTR | Elect | Labour | SWR10628 | 12128 | EA | 24256
24 | 1 | Loading 220 V Battery with Charger | Elect | Labour | SWR11166 | 1692 | SET | 1692
25 | 1 | Un-loading 220 V Battery with Charger | Elect | Labour | SWR11147 | 1075 | SET | 1075
26 | 1 | Erection of 220V Battery with charger incl eart | Elect | Labour | SWR21896 | 7666 | EA | 7666
27 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) | Elect | Labour | SWR10139 | 2667 | KM | 2667
28 | 16 | Erection of 11KV indoor switchgear panel | Elect | Labour | SWR10931 | 8894 | EA | 142304
29 | 16 | Loading of 11 KV VCBs&Panel boards | Elect | Labour | SWR10199 | 1075 | EA | 17200
30 | 16 | Unloading of 11 KV VCBs&Panel boards | Elect | Labour | SWR10517 | 1075 | EA | 17200
31 | 10 | Erection of 33KV indoor switch gear panel/33KV indoor PT panel / Bus section panel / Bus raiser panel | Elect | Labour | SWR10930 | 9847 | EA | 98470
32 | 10 | LOADING of 33 KV VCBs&Panel boards | Elect | Labour | SWR10198 | 1075 | EA | 10750
33 | 10 | UNLOADING of 33 KV VCBs&Panel boards | Elect | Labour | SWR10516 | 1075 | EA | 10750
34 | 26 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) | Elect | Labour | SWR10139 | 2667 | KM | 69342
35 | 6 | Erection of RS Joist Girder pole 150X150mm | Elect | Labour | SWR10348 | 1407 | EA | 8442
36 | 8 | Erection of RS Joist 175 x 85 mm | Elect | Labour | SWR10346 | 1690.5 | EA | 13524
37 | 17.6 | Laying of foudation with RCC for VCB Plinths (33KV, 11KV & PTR Plinth), as per the drawing (2.2 X 2.2 X 1.5 mtrs), Providing of Concreting (2 X 2 X 1.5 mtrs) with 1:3:6 Concrete mix, size provinding of concreting for PTR ( 3.0M x 3.0M x 1.65M)is as shown in the drawings, Providing the foundation boils (20mm) suitable to VCB Structure plastering of the plinth for smooth finishing with 12mm thick 1:2 cement mortor and providing two coats of white washing for part of te plinth above ground level | Elect | Labour | SWR30007 | 5788 | M3 | 101868.8
38 | 17.6 | Earth work excavation for foundation of VCB etc | Elect | Labour | SWR10857 | 331 | M3 | 5825.6
39 | 7.5 | Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Supply | SMR40009 | 2181 | TO | 16357.5
40 | 7.5 | Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 6382.5
41 | 7.5 | Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Supply | SMR40010 | 1293 | TO | 9697.5
42 | 7.5 | Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 3615
43 | 50 | Painting of Name Plates for any equipment | Elect | Labour | SWR10963 | 122 | EA | 6100
44 | 1 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 142
45 | 6 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Elect | Supply | SMR40051 | 14609 | EA | 87654
46 | 6 | Errection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 8274
47 | 6 | Supply of 150 W Metal halide lamps with fixtures.. | Elect | Supply | SMR40056 | 6450 | EA | 38700
48 | 6 | Fixing of Metal halide lamps with fixtures Make:Philips,Crompton,Bajaj junction box with MCB with 1.5 GI pipe complete. | Elect | Labour | SWR10956 | 1268 | EA | 7608
49 | 2 | Supply of Copper Flexible jumper with 75 X 8 of length 250 mm at neutral of Power tranformer end and 50 X 6 of length 50mm two Nos at double neutral end duly brasing with flexible jumper of capacity of 5kA/3 sec for power transformer neutral. | Elect | Supply | SMR40033 | 5209 | EA | 10418
50 | 1700 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Elect | Labour | SWR21301 | 14 | LS | 23800
51 | 1 | Supply of AC Supply panel inluding providing of changeover switch, SFU, metering unit, 32 A three phase MCB, 16 A Single phase MCB complete as per specification. | Elect | Supply | SMR40045 | 44100 | EA | 44100
52 | 1 | Erection of control/Relay panels, AC Panels, announciation panels etc in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts. | Elect | Supply | SWR21311 | 2122 | LS | 2122
53 | 750 | Supplying & fabrication erection of 6mm Checkerd plates as per the field conditions | Elect | Supply | SWR10873 | 83 | KG | 62250
54 | 12 | Supply Rubber mats( 6#x3#)size for indoorSS | Elect | Supply | SMR40068 | 1455 | EA | 17460
55 | 1 | Sup Alluminium Ladder for indoor works | Elect | Supply | SMR40062 | 4410 | EA | 4410
56 | 2 | Supply of TrollyMounted Co2 Cylinders(IS-2878) | Elect | Supply | SMR40087 | 9702 | EA | 19404
57 | 2 | Supply of Fire Buckets Stand with Buckets | Elect | Supply | SMR40088 | 1455 | SET | 2910
58 | 6 | Supply of Fire Extinguisher for Control Room | Elect | Supply | SMR40089 | 4851 | EA | 29106
59 | 4 | Supply of Safety Helmet of standard make | Elect | Supply | SMR40071 | 243 | EA | 972
60 | 4 | Supply Earth Rods (8ft) Screw & clamp type | Elect | Supply | SMR40066 | 607 | EA | 2428
61 | 4 | Supply of Hand Gloves | Elect | Supply | SMR40067 | 331 | SET | 1324
62 | 1 | Supply of Stand basic cell phone with charger | Elect | Supply | SMR40069 | 1455 | EA | 1455
63 | 1 | Supply of Steel almarah(61/2 X 3ft) Godrej | Elect | Supply | SMR40061 | 11339 | EA | 11339
64 | 1 | Supply of Table (3x6ft) Godrej | Elect | Supply | SMR40057 | 6671 | EA | 6671
65 | 4 | Supply of S type chairs (Godrej) | Elect | Supply | SMR40058 | 1067 | EA | 4268
66 | 1 | Supply of Angle racks(18x36.6inches) Godrej | Elect | Supply | SMR40060 | 2001 | EA | 2001
67 | 10 | Supply of Danger boards with clamps | Elect | Supply | SMR40070 | 122 | EA | 1220
68 | 1 | Supply of Name board of the 33/11kV Sub-Station(As per Standard Specification) | Elect | Supply | SMR40086 | 10750 | EA | 10750
69 | 1 | Supply of Wall clock standard make | Elect | Supply | SMR40059 | 667 | EA | 667
70 | 1 | Supply of Taparia Tool kit of Size 20”x10”x15” with tier arrangements Tool box with locking arrangement & key containing (1) Double Ended fix Spanner sets, (Ribbed) 6 x 7, 8 x 9, 10 x 11, 12 x 13, 14 x 15, 16 x 17, 18 x19, 20 x 22, 21 x 23, 24 x 27, 25 x28, 30 x 32, (2) Double Ended Ring Spanners sets, 6 x 7 , 8 x 9, 10 x 11, 12 x 13, 14 x 15. 16 x 17 , 18 x 19, 20 x 22 , 21 x 23, 24 x 27, 25 x28, 30 x 32 mm, (3) Adjustable Spanner 305 mm length least maximum opening 35mm chrome, (4) Pipe Wrench Length 350 mm 14”, (5) Soft faced Hammer with suitable handle 2 lb, (6) Hacksaw frame with metal handle heavy duty for 12" hacksaw blade with High Speed blade, (7) Insulated Screw drivers Transparent Green Handle Set Length 6”, 8” & 12”, (8) Star Screw Driver Transparent Green Handle Length 6”, (9) Insulated Wire Cutter, (10) Insulated Cutting Plier Length 8” with cable stripper insulated with thick C. A. sleeve confirming to IS: 4378 - 1990, (11) Long Nose Plier insulated with thick C.A. sleeve generally confirming to IS:3552-1989, (12) Tester type screw driver (special with neon bulb) generally confirm to IS: 5579-1985 Grade:II handle yellow/ green colour overall length 130 mm, (13) Insulated Crimping Plier of all Taparia make. | Elect | Supply | SMR40063 | 9096 | SET | 9096
71 | 1 | Supply of Rechargeable LED torch light. | Elect | Supply | SMR40064 | 1820 | EA | 1820
72 | 1 | Supply of Hack saw (12 inches) | Elect | Supply | SMR40065 | 303 | EA | 303
73 | 8 | Supply of LC Boards | Elect | Supply | SMR40072 | 122 | EA | 976
74 | 2 | Supply of Gum Boots | Elect | Supply | SMR40073 | 728 | EA | 1456
75 | 1 | Supply of Digital clamp meter. | Elect | Supply | SMR40076 | 3032 | EA | 3032
76 | 1 | Supply of 5000v megger | Elect | Supply | SMR40074 | 14553 | EA | 14553
77 | 1 | Supply of Aluminium ladder(10 feet) | Elect | Supply | SMR40007 | 1654 | EA | 1654
78 | 1 | Supply and fixing of Substation board of size 3'x2.5' indicating the layout of switchyard | Elect | Labour | SWR20032 | 1654 | EA | 1654
79 | 1 | Supply and fixing of safety instructions/Substation operation instruction board | Elect | Labour | SWR22090 | 2205 | EA | 2205
80 | 36 | Cost of CI earth pipe 100 mm dia, 2.75 mt long with flange | Elect | Supply | SMR11482 | 3494 | EA | 125784
81 | 36 | Excavation of earth pit, putting cast iron pipe with flange on one end of nominal dia 100mm and 2.75 meters long in side the pit including supply and fixing RCC collars 0.75 meter dia (OD), 50mm thick and 0.60meters long in side the pit, backfill the pit with bentonite & black cotton soil mix for full depth of the pit with alternate layers of of 300mm thick around the earth pipe of 150mm on all the sides of the pipe including cost and conveyance of bentonite, Black cotton soil, clamps, C.I.Pipes and RCC collars, labour charges for all operational and incidental items of work etc., complete. | Elect | Labour | SWR10923 | 2122 | EA | 76392
82 | 2 | Excavation of earth pit, putting GI pipe with suitable clamp of nominal dia 40mm and 2.0meters long in side the pit including supply and fixing RCC collars 0.75 meter dia (OD), 50mm thick and 0.60meters long in side the pit, backfill the pit with bentonite & black cotton soil mix for full depth of the pit with alternate layers of of 300mm thick around the earth pipe of 150mm on all the sides of the pipe including cost and conveyance of bentonite, Black cotton soil, clamps, G.I.Pipe and RCC collars, labour charges for all operational and incidental items of work etc., complete. | Elect | Labour | SWR20182 | 1152 | EA | 2304
83 | 2 | Supply of GI eath pipe with 40 mm dia,3mm thcikness with 2.0 M Length | Elect | Supply | SMR11480 | 733 | EA | 1466
84 | 464 | Laying of earth mat at EHT SS -75x 8mm MS Flat / GI Flat. | Elect | Labour | SWR10920 | 68 | RMT | 31552
85 | 375 | Laying of Earth mat 50x6mm Flat | Elect | Labour | SWR21170 | 68 | M | 25500
86 | 500 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Elect | Labour | SWR20813 | 27 | LS | 13500
87 | 2 | Fabrication and laying of ladder in cable trench | Elect | Labour | SWR22088 | 827 | EA | 1654
88 | 10 | Fixing of 105lb rail poles over the transformer plinths. | Elect | Labour | SWR10872 | 471 | RMT | 4710
89 | 34 | Loading of 11/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1075 | DR | 36550
90 | 34 | Unloading of 11/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1075 | DR | 36550
91 | 17 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) upto 10km | Elect | Labour | SWR10139 | 2667 | KM | 45339
Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.
92 | 1100 | Laying of 33 KV 3x400 Sqmm Cable In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC | Elect | Labour | SWR10835 | 585 | M | 643500
93 | 1600 | Laying of 33 KV 3x400 Sqmm Cable Along the CC / BT multi layer road requiring compressor | Elect | Labour | SWR10766 | 1085 | EA | 1736000
94 | 900 | Laying of 33 KV 3x400 Sqmm Cable -Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) | Elect | Labour | SWR10772 | 1240 | EA | 1116000
95 | 1000 | Laying of 33KV XLPE UG cable Double Run of Size in Hard Rock(1.2*0.5x1=0.6cum) | Elect | Labour | SWR11002 | 1430 | RMT | 1430000
96 | 400 | Raising of 33KV XLPE UG cable Double run cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR22094 | 254 | M | 101600
97 | 4600 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 91 | M | 418600
98 | 22 | Making of 33 KV 3x400 Sqmm Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10387 | 2310 | EA | 50820
99 | 22 | Making of 33 KV 3x400 Sqmm Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10387 | 2310 | EA | 50820
100 | 60 | Making of 33 KV 3x400 Sqmm Cable Straight through joints kits | Elect | Labour | SWR10382 | 4764 | EA | 285840
101 | 1600 | Supply of 250 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | Elect | Supply | SMR40077 | 363 | M | 580800
102 | 3500 | Supply of 6" B class GI pipe | Elect | Supply | SMR40081 | 1044 | M | 3654000
103 | 1500 | Supply of 6" DWC pipe | Elect | Supply |  | 1012 | M | 1518000
104 | 28 | Loading of 11/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11230 | 1075 | DR | 30100
105 | 28 | Unloading of 11/33KV XLPE UG Cable for all sizes | Elect | Labour | SWR11231 | 1075 | DR | 30100
106 | 14 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) upto 10km | Elect | Labour | SWR10139 | 2667 | KM | 37338
Laying of XLPE UG cable Triple or more Run including excavation of trench of size 1000mm wide to 750mm wide as per the site conditions and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second,third or more cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.
107 | 250 | Laying 11KV XLPE UG Cable Triple run and above in Hard rock | Elect | Labour |  | 2144 | RMT | 536000
108 | 340 | Laying of 11 KV 3x300 / 3x185 / 3x95 Sqmm Cable, Triple run In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC | Elect | Labour | SWR22071 | 612 | M | 208080
109 | 260 | Laying of 11 KV 3x300 / 3x185 / 3x95 Sqmm Cable, Triple run Along the CC / BT multi layer road requiring compressor | Elect | Labour | SWR22075 | 1238 | M | 321880
110 | 150 | Laying of 11 KV 3x300 / 3x185 / 3x95 Sqmm Cable, Triple run Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) | Elect | Labour | SWR22079 | 1416 | M | 212400
111 | 2000 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 91 | M | 182000
Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and lift etc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.
112 | 450 | Laying of 11 KV 3x300 / 3x185 / 3x95 Sqmm Cable, Double run Along the CC / BT multi layer road requiring compressor | Elect | Labour | SWR10767 | 988 | EA | 444600
113 | 210 | Laying of 11 KV 3x300 / 3x185 / 3x95 Sqmm Cable, Double run Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) | Elect | Labour | SWR10773 | 1132 | EA | 237720
114 | 350 | Laying of11KV XLPE UG cable Double Run of Size in Hard Rock(1.05*0.5x1=0.525cum) | Elect | Labour | SWR11004 | 1194 | RMT | 417900
115 | 190 | Laying of 11 KV 3x300 / 3x185 / 3x95 Sqmm Cable, Double run In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC | Elect | Labour | SWR10836 | 493 | M | 93670
116 | 1200 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 91 | M | 109200
Laying of XLPE UG cable Single Run including excavation of trench of size 450mm wide and 850mm for LT, 1050mm for 11 KV and 1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc.depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs.
117 | 1150 | Laying of 11 KV 3x300 / 3x185 / 3x95 Sqmm Cable, Single run Along the CC / BT multi layer road requiring compressor | Elect | Labour | SWR10747 | 839 | M | 964850
118 | 730 | Laying of 11 KV 3x300 / 3x185 / 3x95 Sqmm Cable, Single run Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe) | Elect | Labour | SWR10753 | 937 | M | 684010
119 | 470 | Laying of 11KV XLPE UG cable Single Run in Hard Rock(1.05*0.45x1=0.4725cum) | Elect | Labour | SWR11005 | 1075 | RMT | 505250
120 | 250 | Laying of 11 KV 3x300 / 3x185 / 3x95 Sqmm Cable, Single run In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil/CC | Elect | Labour | SWR20846 | 363 | M | 90750
121 | 500 | Raising of cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) -11 KV 3x300 Sqmm Cable | Elect | Labour | SWR10448 | 113 | M | 56500
122 | 35 | Making of 11 KV 3x300 Sqmm Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10391 | 2021 | EA | 70735
123 | 42 | Making of 11 KV 3x300 Sqmm Cable Straight through joints kits | Elect | Labour | SWR10386 | 3176 | EA | 133392
124 | 1000 | Supply of 150 mm Hume pipe of class NP3 with compresive strength of 35N/mm2 for 28 days curing,barewall thickness of 30mm,1.25kG linear/meter and withstanding capability of 22.50KN/linear meter as per IS 458-1993. | Elect | Supply | SMR40078 | 303 | M | 303000
125 | 800 | Supply of 4" B class GI pipe | Elect | Supply | SMR40080 | 740 | M | 592000
126 | 600 | Supply of 4" DWC pipe | Elect | Supply |  | 759 | M | 455400
127 | 9000 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 270000
128 | 9000 | Consultation charges for pursuing with various Departments for obtaining required permissions for Road cutting and submission of necessry Documents, Drawings etc. | Elect | Labour |  | 30 | M | 270000
129 | 9 | LOADING of 11 KV AB Switch Con 200/400 A | Elect | Labour | SWR10238 | 82 | EA | 738
130 | 9 | UNLOADING of 11 KV AB Switch Con 200/400 A | Elect | Labour | SWR10556 | 82 | EA | 738
131 | 6 | LOADING of 33 KV AB Switch Con 400/800 A | Elect | Labour | SWR10239 | 146 | EA | 876
132 | 6 | UNLOADING of 33 KV AB Switch Con 400/800 A | Elect | Labour | SWR10557 | 91 | EA | 546
133 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) upto 10km | Elect | Labour | SWR10139 | 2667 | KM | 2667
134 | 6 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 2103 | EA | 12618
135 | 9 | Erection of 11 KVAB Switch 400/200 A conventional type including alignment and earthing | Elect | Labour | SWR10393 | 1641 | EA | 14769
136 | 8.8 | Laying of foudation with RCC for VCB Plinths (33KV, 11KV & PTR Plinth), as per the drawing (2.2 X 2.2 X 1.5 mtrs), Providing of Concreting (2 X 2 X 1.5 mtrs) with 1:3:6 Concrete mix, size provinding of concreting for PTR ( 3.0M x 3.0M x 1.65M)is as shown in the drawings, Providing the foundation boils (20mm) suitable to VCB Structure plastering of the plinth for smooth finishing with 12mm thick 1:2 cement mortor and providing two coats of white washing for part of te plinth above ground level | Elect | Labour | SWR30007 | 5788 | M3 | 50934.4
137 | 8.8 | Earth work excavation for foundation of VCB etc | Elect | Labour | SWR10857 | 331 | M3 | 2912.8
138 | 5 | Coping&muffing of iron poles | Elect | Labour | SWR20584 | 3893 | EA | 19465
139 | 5 | Fabrication of Box pole | Elect | Labour | SWR20749 | 615 | EA | 3075
140 | 5 | Erection of Box Pole | Elect | Labour | SWR20587 | 2257.5 | EA | 11287.5
141 | 5 | LOADING of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 73 | EA | 365
142 | 5 | UNLOADING of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 49 |  | 245
143 | 5 | Painting of RS Joist(1C RO, 2C Al.Paint) | Elect | Labour | SWR10640 | 1149 | EA | 5745
144 | 9 | Excavation of earth pit, putting GI pipe with suitable clamp of nominal dia 40mm and 2.0meters long in side the pit including supply and fixing RCC collars 0.75 meter dia (OD), 50mm thick and 0.60meters long in side the pit, backfill the pit with bentonite & black cotton soil mix for full depth of the pit with alternate layers of of 300mm thick around the earth pipe of 150mm on all the sides of the pipe including cost and conveyance of bentonite, Black cotton soil, clamps, G.I.Pipe and RCC collars, labour charges for all operational and incidental items of work etc., complete. | Elect | Labour | SWR20182 | 1152 | EA | 10368
145 | 9 | Supply of GI pipe of 40 mm dia 2 mtrs | Elect | Supply | SMR40091 | 667 | EA | 6003
146 | 450 | Laying of earth mat,excavation 25x3mm | Elect | Labour | SWR10921 | 81 | RMT | 36450
147 | 11 | Coil earthing of pole with No.8 GI wire | Elect | Labour | SWR22091 | 386 | EA | 4246
148 | 2 | Cost of CI earth pipe 100 mm dia, 2.75 mt long with flange | Elect | Supply | SMR11482 | 3494 | EA | 6988
149 | 2 | Excavation of earth pit, putting cast iron pipe with flange on one end of nominal dia 100mm and 2.75 meters long in side the pit including supply and fixing RCC collars 0.75 meter dia (OD), 50mm thick and 0.60meters long in side the pit, backfill the pit with bentonite & black cotton soil mix for full depth of the pit with alternate layers of of 300mm thick around the earth pipe of 150mm on all the sides of the pipe including cost and conveyance of bentonite, Black cotton soil, clamps, C.I.Pipes and RCC collars, labour charges for all operational and incidental items of work etc., complete. | Elect | Labour | SWR10923 | 2122 | EA | 4244
150 | 6 | Const. of plinth for mount new 3Way RMU | Elect | Labour |  | 6540 | EA | 39240
151 | 6 | Erection of 11KV 3 Way RMU | Elect | Labour | SWR10664 | 1322.5 | EA | 7935
152 | 5 | Erection of RS Joist 175 x 85 mm | Elect | Labour | SWR10346 | 1690.5 | EA | 8452.5
153 | 6 | Supply of 33kV TC Structure as per DATA-II | Elect | Supply | SMR40102 | 49708 | EA | 298248 | 201
154 | 6 | Erection of 33kV TC Structure as per DATA-II | Elect | Labour | SWR11010 | 16240 | EA | 97440
155 | 12 | Supply of 33kV BD Boom as per DATA-IV | Elect | Supply | SMR40104 | 17886 | EA | 214632
156 | 12 | Erection of 33kV BD Boom as per DATA-IV | Elect | Labour | SWR10875 | 495 | EA | 5940
157 | 2 | Supply of 33kV TD Structure as per DATA-I | Elect | Supply | SMR40101 | 20534 | EA | 41068
158 | 2 | Erection of 33kV TD Structure as per DATA-I | Elect | Labour | SWR11009 | 13856 | EA | 27712
159 | 2 | Erection of 33kv ABSwitch incl earthing | Elect | Labour | SWR10392 | 2103 | EA | 4206
160 | 0.2 | Supply of Zebra conductor | Elect | Supply |  | 299369 | KM | 59873.8
161 | 2 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | SET | 1760
162 | 1 | LOADING of 33 KV VCBs&Panel boards | Elect | Labour | SWR10198 | 1075 | EA | 1075
163 | 1 | UNLOADING of 33 KV VCBs&Panel boards | Elect | Labour | SWR10516 | 1075 | EA | 1075
164 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters (which are less in weight and occupy more space) (excluding of loading unloading) | Elect | Labour | SWR10139 | 2667 | KM | 2667
165 | 1 | Erection of 33kV Twin feeder control & Relay panel in the control room duly mounting them on channels and grouting them with foundation bolts excluding cost of channels & foundation bolts | Elect | Labour | SWR10934 | 1906 | EA | 1906
166 | 2 | LOADING of 33 KV AB Switch Con 400/800 A | Elect | Labour | SWR10239 | 146 | EA | 292
167 | 2 | UNLOADING of 33 KV AB Switch Con 400/800 A | Elect | Labour | SWR10557 | 91 | EA | 182
168 | 2 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) UPTO 10KM | Elect | Labour | SWR10131 | 303 | TO | 606
169 | 1 | Erection of 33 KV VCB with Control Panel | Elect | Labour | SWR10460 | 5022 | EA | 5022
170 | 1 | Erection of 33kv CT s | Elect | Labour | SWR10399 | 1133 | SET | 1133
171 | 5.4 | Earth work excavation for foundation of VCB etc | Elect | Labour | SWR10857 | 291 | M3 | 1571.4
172 | 7.26 | Laying of foudation with RCC for VCB Plinths (33KV, 11KV & PTR Plinth), as per the drawing (2.2 X 2.2 X 1.5 mtrs), Providing of Concreting (2 X 2 X 1.5 mtrs) with 1:3:6 Concrete mix, size provinding of concreting for PTR ( 3.0M x 3.0M x 1.65M)is as shown in the drawings, Providing the foundation boils (20mm) suitable to VCB Structure plastering of the plinth for smooth finishing with 12mm thick 1:2 cement mortor and providing two coats of white washing for part of te plinth above ground level | Elect | Labour | SWR30007 | 5788 | M3 | 42020.88
173 | 3 | Plastering 2 coats, 20/16 mm (1:6)/(1:4) | Elect | Labour | SWR10862 | 373 | M2 | 1119
174 | 9 | Conn. of equip/bus single zebra/panther | Elect | Labour | SWR10884 | 224 | EA | 2016
175 | 3 | Supply&Erec of CI earth Pipe as APTRANCO | Elect | Labour | SWR10924 | 10784 | EA | 32352
176 | 60 | Earthing for raisers of SS Flat 50x6 mm. | Elect | Labour | SWR10919 | 41 | RMT | 2460
177 | 520 | SupEarth mat-100X16mm GI Flat-earth pits | Elect | Supply | SMR40093 | 975 | M | 507000
178 | 41 | Laying of earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment and connecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes with the following sizes of MS Flats /GI Flats. including fabrication.-100x16mm M.S./G.I earth flat | Elect | Labour | SWR22054 | 68 | RMT | 2788
179 | 12 | Hoisting of Insl. 2 Zebra/Phanther 33kV | Elect | Labour | SWR10882 | 1302 | EA | 15624
180 | 18 | With Single Zebra without PASD. | Elect | Labour |  | 338.62 | EA | 6095.16
181 | 3 | With Single Zebra with PASD. | Elect | Labour |  | 828.78 | EA | 2486.34
182 | 3 | With Twin Zebra with PASD. | Elect | Labour |  | 1263.91 | EA | 3791.73
183 | 3 | Supply of Spacer T- clamps -Twin zebra/Panther | Elect | Supply | SMR40012 | 533 | EA | 1599
184 | 3 | Supply of Spacer T-clamps dble dppr zebra/Pant | Elect | Supply | SMR40013 | 827 | EA | 2481
185 | 12 | Supply of Tension Hardw 3 Bolt 2Zebra/panther | Elect | Supply | SMR40016 | 2638 | SET | 31656
186 | 24 | Supply of Pad clamp 75X75X15mm 1 panther 600A | Elect | Supply | SMR40018 | 238 | SET | 5712
187 | 6 | Supply of CT stud clamps 1Zebra/Panth for 800A | Elect | Supply | SMR40023 | 419 | EA | 2514
188 | 6 | Supply of U-Bolts 16 mm | Elect | Supply | SMR40040 | 39 | EA | 234
189 | 1 | Supply of FRP CT Marshalling Box | Elect | Supply | SMR40046 | 4355 | EA | 4355
190 | 1 | Erection of Marshalling boxes | Elect | Labour | SWR10940 | 294 | EA | 294
191 | 100 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per specification (including cost of ferrules, lugs and glands) | Elect | Labour | SWR20813 | 27 | LS | 2700
192 | 2 | Supply of stepped tubular poles single way made of steel of length 9mtrs with tensile strength of 42kgf/mm2 at a steps of 4.5 mtrs with outer dia 114.3 mm,2.1 mtrs with outer dia 88.9 mm, 2.1 mtrs with outer dia 76.1 mm, normal Crippling load of 141 kgf, normal Breaking load of 198 kgf ,working Crippling load of 70 kgf, working Breaking load of 79 kgf as per IS 2713. | Elect | Supply | SMR40051 | 14609 | EA | 29218
193 | 2 | Errection of tubular poles | Elect | Labour | SWR10955 | 1379 | EA | 2758
194 | 2 | Supply of 150 W Metal halide lamps with fixtures.. | Elect | Supply | SMR40056 | 6450 | EA | 12900
195 | 1.76 | Earth work excavation for foundation of VCB etc | Elect | Labour | SWR10857 | 331 | M3 | 582.56
196 | 1.76 | Laying of foudation with RCC for VCB Plinths (33KV, 11KV & PTR Plinth), as per the drawing (2.2 X 2.2 X 1.5 mtrs), Providing of Concreting (2 X 2 X 1.5 mtrs) with 1:3:6 Concrete mix, size provinding of concreting for PTR ( 3.0M x 3.0M x 1.65M)is as shown in the drawings, Providing the foundation boils (20mm) suitable to VCB Structure plastering of the plinth for smooth finishing with 12mm thick 1:2 cement mortor and providing two coats of white washing for part of te plinth above ground level | Elect | Labour | SWR30007 | 5877 | M3 | 10343.52
197 | 60 | Labour charges for Fixing of all types of clamps | Elect | Labour | SWR10917 | 65 | EA | 3900
198 | 1000 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends . | Elect | Labour | SWR21301 | 14 | LS | 14000
| Sub Total: | [6 empty] | 22313193.99
| 18% Service tax on labour | [6 empty] | 4016374.9182
| Total Rs. | [6 empty] | 26329568.9082