## Miralam
SCHEDULE
Name of the Work :- Providing of 3rd alternate source to 33/11KV Miralam SS from 132/33KV Mailardevpally EHT SS byerection of new 33KV feeder with laying of 4.8KM of 33KV 3X400Sq.mm. XLPE UG Cable (double run) from the EHT SS to 33/11KV Miralam SS in Hyderabad South operation division of Hyderabad South Circle and the work executed bythe Master Plan SD-III of Division-II in Masterplan Hyderabad Circle under T&D Improvement works (Summer Action Plan 2025)
WBS Element :- T-2427-12-02-03-01-002
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 4.8 | Survey line&cabl inc peg mark,tree clear&trail pits | Elect | Labour | SWR22092 | 765 | KM | 3672
2 | 33 | Loading of 11KV/33KV XLPE UG Cable Drums for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 33792
3 | 17 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excludingof loading unloading)- Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 56094.9
4 | 33 | Un loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 33792
5 | 2500 | Excavation & laying of UG Cable (Double Run) - Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally 4" for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and liftetc - (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs &33 KV - 1.20 mtrs.- Along the CC / BT multi layer road requiring compressor - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11980 | 1388.84 | M | 3472100
6 | 200 | Excavation & laying of UG Cable (Double Run) - Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally 4" for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and liftetc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs &33 KV - 1.20 mtrs.-.Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe)-33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11988 | 1587.07 | M | 317414
7 | 2000 | Laying of 33KV XLPE UG cable Double Run of Size in HardRock (1.2*0.5x1=0.6cum) | Elect | Labour | SWR11002 | 1430 | RMT | 2860000
8 | 2700 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 204.1 | M | 551070
9 | 200 | Laying of 33&11KV UG cable by HDD method with casing HDPE pipe of 160mm PN4 PE 80 as per IS4984 | Elect | Labour | SWR11001 | 6993 | M | 1398600
10 | 45 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 123525
11 | 30 | Making of 33KV 3X400Sq.mm XLPE UG Cable Straight through joints | Elect | Labour | SWR10382 | 5700.78 | EA | 171023.4
12 | 2000 | Supply 6" B Class GI pipe 5mm thck 20Kg/M | Elect | Supply | SMR40081 | 1044 | M | 2088000
13 | 1200 | supply of 6" DWC pipe | Elect | Supply | SMR11610 | 1012 | M | 1214400
14 | 400 | Supply of Hume Pipe Size 9" size | Elect | Supply | SMR40001 | 125 | M | 50000
15 | 16 | Making of 33KV 3X400Sq.mm XLPE UG Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 44236.16
16 | 60 | Raising of double run 33KV 3x400sqmm UG cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR12004 | 323.85 | M | 19431
17 | 4000 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 120000
18 | 45 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters, CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 21780
19 | 1.35 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 298.35
20 | 1.35 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 249.75
21 | 18 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1368
22 | 5.85 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 2410.668
23 | 18 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 900
24 | 6 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 3075.3
25 | 18 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 20376
26 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 5944.08
27 | 3 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting. - Erection of 33 KV DP Structure with 175x85/150x75mm RS joist | Elect | Labour | SWR11276 | 5670 | SET | 17010
28 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - RS Joist 175 x 85 mm | Elect | Labour | SWR10346 | 1934 | EA | 11604
29 | 155 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 6355
30 | 9.54 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 62763.66
31 | 0.186 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 724.098
32 | 0.98 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 3357.48
33 | 3 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | EA | 378
34 | 3 | Un loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | EA | 237
35 | 3 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 13500
36 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 439.89
37 | 3 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 426
38 | 9 | Loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10266 | 41 | EA | 369
39 | 9 | Un loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10584 | 35 | EA | 315
40 | 3 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | SET | 2640
41 | 6 | Supply of CI eath pipe with 80mm dia,2.0 M Length | Elect | Supply | SMR11483 | 2789 | EA | 16734
42 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 7405.2
43 | 6 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 2316
44 | 3 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 159
45 | 30 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 3525
46 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 5568
Total: | [7 empty] | 12769378.936 | 12769378.936
GST @ 18 % | [7 empty] | 2298488.2085 | 2298488.2085
Grand Total: | [7 empty] | 15067867.1445 | 15067867.1445
[5 empty] | 9720 |  | EMD | 301357.3429 | 301357.3429
|  |  | 4.9 |  | 4860
|  |  | 1.225 |  |  |  | cable L | 4700
1175