## T-2427-12-02-03-01-001
SCHEDULE
Name of the Work :- Providing of 3rd alternate source to 33/11KV CRPF SS from 132/33KV Mailardevpally EHT SS by erection of new 33KV feeder with laying of 6.8KM of 33KV 3X400Sq.mm. XLPE UG Cable (double run) from the EHT SS to 33/11KV CRPF SS in Hyderabad South operation division of Hyderabad South Circle and the work executed by the Master Plan SD-III of Masterplan Division-II in Masterplan Hyderabad Circle under T&D Improvement works (Summer Action Plan-2025)
WBS Element :- T-2427-12-02-03-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 6.8 | Survey line&cabl inc peg mark,tree clear&trail pits | Elect | Labour | SWR22092 | 765 | KM | 5202
2 | 46 | Loading of 11KV/33KV XLPE UG Cable Drums for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 47104
3 | 23 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excludingof loading unloading)- Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 75893.1
4 | 46 | Un loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 47104
5 | 3800 | Excavation & laying of UG Cable (Double Run) - Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally 4" for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and liftetc - (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs &33 KV - 1.20 mtrs.- Along the CC / BT multi layer road requiring compressor - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11980 | 1388.84 | M | 5277592
6 | 250 | Excavation & laying of UG Cable (Double Run) - Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally 4" for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and liftetc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs &33 KV - 1.20 mtrs.-.Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe)-33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11988 | 1587.07 | M | 396767.5
7 | 2750 | Laying of 33KV XLPE UG cable Double Run of Size in HardRock (1.2*0.5x1=0.6cum) | Elect | Labour | SWR11002 | 1430 | RMT | 3932500
8 | 4050 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 204.1 | M | 826605
9 | 68 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 186660
10 | 44 | Making of 33KV 3X400Sq.mm XLPE UG Cable Straight through joints | Elect | Labour | SWR10382 | 5700.78 | EA | 250834.32
11 | 3000 | Supply 6" B Class GI pipe 5mm thck 20Kg/M | Elect | Supply | SMR40081 | 1044 | M | 3132000
12 | 1000 | supply of 6" DWC pipe | Elect | Supply | SMR11610 | 1012 | M | 1012000
13 | 500 | Supply of Hume Pipe Size 9" size | Elect | Supply | SMR40001 | 125 | M | 62500
14 | 16 | Making of 33KV 3X400Sq.mm XLPE UG Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 44236.16
15 | 60 | Raising of double run 33KV 3x400sqmm UG cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR12004 | 323.85 | M | 19431
16 | 6600 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 198000
17 | 68 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters, CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 32912
18 | 1.35 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 298.35
19 | 1.35 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 249.75
20 | 18 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1368
21 | 5.85 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 2410.668
22 | 18 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 900
23 | 6 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 3075.3
24 | 18 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 20376
25 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 5944.08
26 | 3 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting. - Erection of 33 KV DP Structure with 175x85/150x75mm RS joist | Elect | Labour | SWR11276 | 5670 | SET | 17010
27 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - RS Joist 175 x 85 mm | Elect | Labour | SWR10346 | 1934 | EA | 11604
28 | 155 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 6355
29 | 9.54 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 62763.66
30 | 0.186 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 724.098
31 | 0.98 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 3357.48
32 | 3 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | EA | 378
33 | 3 | Un loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | EA | 237
34 | 3 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 13500
35 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 439.89
36 | 3 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 426
37 | 9 | Loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10266 | 41 | EA | 369
38 | 9 | Un loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10584 | 35 | EA | 315
39 | 3 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | SET | 2640 |  | 120
40 | 6 | Supply of CI eath pipe with 80mm dia,2.0 M Length | Elect | Supply | SMR11483 | 2789 | EA | 16734 |  | 7600 | 3800
41 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 7405.2 |  | 500 | 250
42 | 6 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 2316 |  | 5500 | 2750
43 | 3 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 159 |  | 13720 | 6800
44 | 30 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 3525 |  |  | 1700
45 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 5568 |  | 6800
Total: | [7 empty] | 15737789.556 | 15737789.56
GST @ 18 % | [7 empty] | 2832802.1201
Grand Total : | [7 empty] | 18570591.6761 | 371411.8335
18570591.6761
371411.8335

## T-2427-12-02-03-01-002
SCHEDULE
Name of the Work :- Providing of 3rd alternate source to 33/11KV Miralam SS from 132/33KV Mailardevpally EHT SS byerection of new 33KV feeder with laying of 4.8KM of 33KV 3X400Sq.mm. XLPE UG Cable (double run) from the EHT SS to 33/11KV Miralam SS in Hyderabad South operation division of Hyderabad South Circle and the work executed bythe Master Plan SD-III of Division-II in Masterplan Hyderabad Circle under T&D Improvement works (Summer Action Plan 2025)
WBS Element :- T-2427-12-02-03-01-002
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 4.8 | Survey line&cabl inc peg mark,tree clear&trail pits | Elect | Labour | SWR22092 | 765 | KM | 3672
2 | 33 | Loading of 11KV/33KV XLPE UG Cable Drums for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 33792
3 | 17 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excludingof loading unloading)- Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 56094.9
4 | 33 | Un loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 33792
5 | 2500 | Excavation & laying of UG Cable (Double Run) - Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally 4" for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and liftetc - (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs &33 KV - 1.20 mtrs.- Along the CC / BT multi layer road requiring compressor - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11980 | 1388.84 | M | 3472100
6 | 200 | Excavation & laying of UG Cable (Double Run) - Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally 4" for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and liftetc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs &33 KV - 1.20 mtrs.-.Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe)-33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11988 | 1587.07 | M | 317414
7 | 2000 | Laying of 33KV XLPE UG cable Double Run of Size in HardRock (1.2*0.5x1=0.6cum) | Elect | Labour | SWR11002 | 1430 | RMT | 2860000
8 | 2700 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 204.1 | M | 551070
9 | 200 | Laying of 33&11KV UG cable by HDD method with casing HDPE pipe of 160mm PN4 PE 80 as per IS4984 | Elect | Labour | SWR11001 | 6993 | M | 1398600
10 | 45 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 123525
11 | 30 | Making of 33KV 3X400Sq.mm XLPE UG Cable Straight through joints | Elect | Labour | SWR10382 | 5700.78 | EA | 171023.4
12 | 2000 | Supply 6" B Class GI pipe 5mm thck 20Kg/M | Elect | Supply | SMR40081 | 1044 | M | 2088000
13 | 1200 | supply of 6" DWC pipe | Elect | Supply | SMR11610 | 1012 | M | 1214400
14 | 400 | Supply of Hume Pipe Size 9" size | Elect | Supply | SMR40001 | 125 | M | 50000
15 | 16 | Making of 33KV 3X400Sq.mm XLPE UG Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 44236.16
16 | 60 | Raising of double run 33KV 3x400sqmm UG cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR12004 | 323.85 | M | 19431
17 | 4000 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 120000
18 | 45 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters, CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 21780
19 | 1.35 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 298.35
20 | 1.35 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 249.75
21 | 18 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1368
22 | 5.85 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 2410.668
23 | 18 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 900
24 | 6 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 3075.3
25 | 18 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 20376
26 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 5944.08
27 | 3 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting. - Erection of 33 KV DP Structure with 175x85/150x75mm RS joist | Elect | Labour | SWR11276 | 5670 | SET | 17010
28 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - RS Joist 175 x 85 mm | Elect | Labour | SWR10346 | 1934 | EA | 11604
29 | 155 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 6355
30 | 9.54 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 62763.66
31 | 0.186 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 724.098
32 | 0.98 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 3357.48
33 | 3 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | EA | 378
34 | 3 | Un loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | EA | 237
35 | 3 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 13500
36 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 439.89
37 | 3 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 426
38 | 9 | Loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10266 | 41 | EA | 369
39 | 9 | Un loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10584 | 35 | EA | 315
40 | 3 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | SET | 2640
41 | 6 | Supply of CI eath pipe with 80mm dia,2.0 M Length | Elect | Supply | SMR11483 | 2789 | EA | 16734
42 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 7405.2
43 | 6 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 2316
44 | 3 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 159
45 | 30 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 3525
46 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 5568
Total: | [7 empty] | 12769378.936
GST @ 18 % | [7 empty] | 2298488.2085
Grand Total: | [7 empty] | 15067867.1445

## Attapur
SCHEDULE
Name of the Work :- Providing of 3rd alternate source to 33/11KV Attapur SS from 132/33KV Seetharambagh Indoor EHT SS by laying of 6.65KM of 3X400Sqmm. XLPE UG Cable (Triple Run, 2No.s 33KV feeders) viz., 2run for providing of alternate source of supply to 33/11KV Attapur SS and 1run for extending regular source of supply to the upcoming 33/11KV STP Plant SS in Hyderabad South operation division of Hyderabad South Circle and work executed by the Master plan SD-III Sub-Division of MP-II Division of Hyderabad Master plan Circle under T& D Improvement Works(Summer Action Plan 2025)
WBS Element :- T-2427-12-02-03-01-003
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 6.65 | Survey line&cabl inc peg mark,tree clear&trail pits | Elect | Labour | SWR22092 | 765 | KM | 5087.25
2 | 67 | Loading of 11KV/33KV XLPE UG Cable Drums for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 68608
3 | 34 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excludingof loading unloading)- Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 112189.8
4 | 67 | Un loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 68608
5 | 3650 | Lay-TR 33KV 3x400sqmm UG Cb CC/BT Compsr | Elect | Labour | SWR12019 | 1731.45 | M | 6319792.5
6 | 250 | Lay-TR 33KV 3x400sqmm UG Cb CC/BT RdCrsg | Elect | Labour | SWR12024 | 1978.8 | M | 494700
7 | 2750 | Lay-33KV XLPE UG Cb Tiple Run in Hrd Rck | Elect | Labour | SWR11800 | 2733.6 | RMT | 7517400
8 | 7800 | Lay-2nd Cable in Excavated Trench | Elect | Labour | SWR10988 | 204.1 | M | 1591980
9 | 66 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | M | 181170
10 | 66 | Making of 33KV 3X400Sq.mm XLPE UG Cable Straight through joints | Elect | Labour | SWR10382 | 5700.78 | EA | 376251.48
11 | 4500 | Supply 6" B Class GI pipe 5mm thck 20Kg/M | Elect | Labour | SMR40081 | 1044 | EA | 4698000
12 | 1500 | supply of 6" DWC pipe | Elect | Supply | SMR11610 | 1012 | M | 1518000
13 | 500 | Supply of Hume Pipe Size 9" size | Elect | Supply | SMR40001 | 125 | M | 62500
14 | 18 | Making of 33KV 3X400Sq.mm XLPE UG Cable Outdoor/Indoor End Termination | Elect | Supply | SWR10387 | 2764.76 | M | 49765.68
15 | 60 | Raising of double run 33KV 3x400sqmm UG cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR12004 | 323.85 | EA | 19431
16 | 60 | Raising of Single run 33KV 3x400sqmm UG cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11954 | 135.66 | M | 8139.6
17 | 6600 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 198000
18 | 66 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters, CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 31944
19 | 480 | Laying of the 33KV cable Single Run along the footpath through by removing & relaying of slabs including material with necessary plastering - 33KV 1x400sqmm Cu Cb FootPathSlab | Elect | Labour | SWR11971 | 308.55 | TO | 148104
20 | 160 | Raising of Single run 33KV 1x400sqmm Copper UG cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11962 | 121.13 | TO | 19380.8
21 | 8 | Supply of 33KV 1Cx400Sqmm Plug Termination Kit | Elect | Labour | SMR24773 | 90915 | EA | 727320
22 | 8 | Installation of 33KV 1Cx400Sqmm Plug Termination Kit | Elect | Labour | SWR24773 | 15675 | TO | 125400
23 | 8 | Supply of 33KV 1Cx400Sqmm O/d Cb End Kit | Elect | Labour | SMR24774 | 6792.5 | EA | 54340
24 | 8 | Installation of 33KV 1Cx400Sqmm O/d Cb End Kit | Elect | Labour | SWR24774 | 3030.5 | EA | 24244
25 | 2.02 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | EA | 446.42
26 | 2.02 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | EA | 373.7
27 | 30 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | SET | 2280
28 | 9.52 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | EA | 3923.0016
29 | 30 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | RMT | 1500
30 | 9 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | M3 | 4612.95
31 | 21 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | M3 | 23772
32 | 9 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95M | Elect | Labour | SWR11040 | 990.68 | TO | 8916.12
33 | 3 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting. - Erection of 33 KV DP Structure with 175x85/150x75mm RS joist | Elect | Labour | SWR11276 | 5670 | EA | 17010
34 | 12 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - RS Joist 175 x 85 mm | Elect | Labour | SWR10346 | 1934 | EA | 23208
35 | 231 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | EA | 9471
36 | 15.93 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | EA | 104803.47
37 | 0.279 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | EA | 1086.147
38 | 1.465 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | EA | 5019.09
39 | 6 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | EA | 756
40 | 6 | Un loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | SET | 474
41 | 6 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Supply | SWR10392 | 4500 | EA | 27000
42 | 6 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 879.78
43 | 6 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 852
44 | 18 | Loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10265 | 32 | EA | 576
45 | 18 | Un loading of 33 KV, 10 KA LAs Station type | Elect | Supply | SWR10583 | 32 | KG | 576
46 | 6 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | DR | 5280
47 | 12 | Supply of CI eath pipe with 80mm dia,2.0 M Length | Elect | Labour | SMR11483 | 2789 | EA | 33468
48 | 12 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | DR | 14810.4
49 | 12 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | M | 4632
50 | 6 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | M | 318
51 | 60 | Supply of GI Bolts & Nuts etc | Elect | Labour | SMR11488 | 117.5 | RMT | 7050
52 | 3 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - 12Meter Box pole | Elect | Labour | SWR11267 | 3901.37 | M | 11704.11
53 | 12 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | M | 11136
54 | 4 | Loading of R.S. Joists 150 x 150mm / Rail poles | Elect | Labour | SWR10205 | 176 | EA | 704
55 | 4 | Un loading of R.S. Joists 150 x 150mm / Rail poles | Elect | Labour | SWR10523 | 107 | EA | 428
56 | 2 | Loading of R.S. Joists 175 x 85 mm | Elect | Supply | SWR10204 | 76 | M | 152
57 | 2 | Un loading of R.S. Joists 175 x 85 mm | Elect | Supply | SWR10522 | 50 | M | 100
58 | 1.561 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Supply | SWR10206 | 221 | M | 344.981
59 | 1.561 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | EA | 288.785
60 | 3.5 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | M | 1442.28
61 | 4 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | M | 3712
62 | 1.15 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Supply | SWR10869 | 3426 | EA | 3939.9
63 | 3.09 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for First coat of 1st Grade Aluminium Paint, brushes etc. | Elect | Labour | SMR40009 | 2181 | TO | 6739.29
64 | 3.09 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. -Labour charges for painting including scratching and cleaning of Sub-station structures of 1st coat of Aluminium | Elect | Labour | SWR10877 | 851 | TO | 2629.59
65 | 3.09 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes, labour charges etc., complete. - Supply of material cost for Second coat of 1st Grade Aluminium Paint, brushes, etc. | Elect | Labour | SMR40010 | 1293 | EA | 3995.37
66 | 3.09 | Painting of sub-station structures with two coats of Aluminium paint using Aluminium paint 1st grade containing 3.6 kg of Aluminium paste for 18 liters of thinner 1st coat is to be applied before erection of sub-station structures and 2nd coat after stringing and half round welding including cost of paint, cost of brushes,labour charges etc., complete- Labour charges for painting including scratching and cleaning of Sub-station structures of 2nd coat of Aluminium . | Elect | Labour | SWR10879 | 482 | TO | 1489.38
67 | 4 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - Erection of RS Joist 150 x 150 mm | Elect | Labour | SWR10348 | 1952.61 | EA | 7810.44
68 | 4.2 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | EA | 27631.8
69 | 2.31 | Plastering 2 Coats,20/16mm(1:6)(1:4) | Elect | Labour | SWR10862 | 373 | EA | 861.63
70 | 4 | Paint of coping with 2 coats of white cement incl cost of paints etc | Elect | Labour | SWR11089 | 48 | EA | 192
71 | 2 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - RS Joist 150 x 150 mm Poles 0.76X0.76X1.52M | Elect | Labour | SWR11037 | 793 | SET | 1586
72 | 2 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - RS Joist 175 x 85 mm | Elect | Labour | SWR10346 | 1934 | EA | 3868
73 | 1.76 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | RMT | 11579.04
74 | 2 | Paint of coping with 2 coats of white cement incl cost of paints etc | Elect | Labour | SWR11089 | 48 | M3 | 96
75 | 3 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | M3 | 378
76 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Labour | SWR11861 | 3299.7 | TO | 3299.7
77 | 3 | Un loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | EA | 237
78 | 3 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 13500
79 | 3 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 426
80 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 439.89
81 | 3 | Loading of 33 KV, 10 KA LAs Line type | Elect | Labour | SWR10265 | 32 | EA | 96
82 | 3 | Un loading of 33 KV, 10 KA LAs Line type | Elect | Labour | SWR10583 | 32 | EA | 96
83 | 1 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | EA | 880
84 | 1 | Loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10198 | 1024 | SET | 1024
85 | 1 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs, control panels, current transformers, boosters, lightning arrestors, insulators, transformers, meters(which are less in weight and occupy more space) Above 10 Km and upto 20 Km | Elect | Supply | SWR11861 | 3299.7 | EA | 3299.7
86 | 1 | Un loading of 33 KV VCBs along with Panel boards | Elect | Labour | SWR10516 | 1044.48 | EA | 1044.48
87 | 4.8 | Earth work excavation of pits in hard murram/rock boulders | Elect | Labour | SWR20959 | 1530 | EA | 7344
88 | 6 | Cement concrete 1:3:6 ration with 40 MML HBG metal including the cost of all materials and labour complete 1.8 x1.8 x 0.75 cum for VCB Plinth | Elect | Labour | SWR20685 | 5160 | EA | 30960
89 | 1 | Erection of 33 KV VCB with Control Panel | Elect | Supply | SWR10460 | 12500 | KG | 12500
90 | 3 | Supply of Tension Hardware 3 Bolted for Twin Zebra/panther with 150 mm spacing | Elect | Labour | SMR40016 | 2512 | EA | 7536
91 | 3 | Supply of I-Bolts | Elect | Labour | SMR22473 | 294 | EA | 882
92 | 6 | Supply of Alluminum alloy T clamps conforming to A6 of IS 617, 4 bolted with hot dip galvanised bolts and double nuts with spring and flat washers of size M10 x 65 i.e(3/8" x 21/2 " to suit for panther ACSR on all three ways /on one side and Zebra ACSR on take off side or any other combination for carrying 800 A current rating . | Elect | Supply | SMR40011 | 299 | KG | 1794
93 | 1 | Hoisting of Insulators and hardware, stretching the conductor and stringing of 33kV bus comprising of three phases with Single Zebra/panther conductor to a tension of 450kgs.(Bus section of 4.5mt) | Elect | Labour | SWR21240 | 781 | DR | 781
94 | 6 | Connection of equipment to bus and or another equipment with single zebra/Panther conductor including measuring, cutting,clamping and hoisting of suspension insulator assembly to support the conductor wherever necessary. | Elect | Labour | SWR10884 | 224 | EA | 1344
95 | 6 | Labour for Fixing of all types of clamps | Elect | Labour | SWR10917 | 65 | DR | 390
96 | 26.5 | Laying of MS Flats /GI Flats 75x 8mm earth mat including excavation of trenches of depth 600mm, welding, connecting to equipment andconnecting lightning shield to earth mat and earthing of fence posts, drilling and connecting earth rods including connecting cast iron pipes including fabrication | Elect | Labour | SWR10920 | 65 | M | 1722.5
97 | 120 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | M | 4920
98 | 4 | Supply of CI earth pipe 100 mm dia, 2.75 mt long thickness 10mm with flange as per specication | Elect | Labour | SMR11482 | 3486 | RMT | 13944
99 | 4 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | M | 4936.8
100 | 4 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | M | 1544
101 | 5 | Providing of control cable trench as per DATA-XII | Elect | Labour | SWR22093 | 3148 | EA | 15740
102 | 306 | Laying of 4 core/10 core 2.5 sq. mm.Copper control cable in aready excavation trench including cost of providing single compress glands at both ends | Elect | Labour | SWR11879 | 27 | EA | 8262
103 | 30 | Cable terminations to the switch gear marshalling boxes/panel terminal blocks/control and relay panels LT AC panel including providing suitable ferrules and lugs as per pecification (including cost of ferrules, lugs and glands) | Elect | Supply | SWR12510 | 27 | M | 810
104 | 5 | Supply & spreading of 20mm machine crushed metal (HBG) including cost of conveneyance of all materials, labour charges etc complete for finished item of work and directed by the engineer incharge | Elect | Supply | SWR10860 | 2113 | M | 10565
105 | 4 | Supply &Fixing of 15mm Bib Tap 300gm Qtr turn | Elect | Supply | SWR34330 | 684 | M | 2736
106 | 20 | Supply &Fixing of 22.20mm OD CPVC Pipe-SDR 11 | Elect | Labour | SWR34362 | 313 | EA | 6260
107 | 2 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | M | 106
108 | 50 | Supply of GI Bolts & Nuts etc | Elect | Labour | SMR11488 | 117.5 | M | 5875
109 | 30 | Laying of 4No's single core 630 sqmm UG cable (Single Circuit with one spare cable) including excavation of trench of size 0.7 Mtrs width and 1.2 Mtrs depth from road level, providing of DWC/GI pipes whereever required depth is not acquired as per the instructions of Engineer in Charge and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, back filling the trench withearth, levelling and and removing the debris from the site inluding the cost of lead and lift etc. In Hard Gravel Soil / BC soil / Red earth / stone and earth mixed with fair boulders / Normal soil | Elect | Supply | SWR12110 | 2463.3 | EA | 73899
110 | 80 | Raise-33KV 33KV 630sqmm UG Cb on support | Elect | Labour | SWR12448 | 133 | TO | 10640
111 | 8 | Supply of 33KV 1x630Sqmm OD Unit EndTermtn | Elect | Labour | SMR12474 | 4200 | TO | 33600
112 | 8 | Installation of 33KV 1x630Sqmm OD Unit EndTermtn | Elect | Labour | SWR12474 | 4000 | EA | 32000
Total: | [7 empty] | 25141692.8546 | 25141692.8546
GST @ 18 % | [7 empty] | 4525504.7138 | 4525504.7138
Grand Total: | [7 empty] | 29667197.5684 | 29667197.5684
[7 empty] | 2% | 593343.9514 | 593343.9514
[5 empty] | 3650 | 7.13
[5 empty] | 250 | 1.7825
2750
6650
19950
180
20130

## T-2431-12-02-03-01-001
SCHEDULE
Name of the Work :- Providing of alternate source of supply to 33/11KV Panjesha SS from 220/132/33KV Chandrayangutta EHT SS by laying of 2.5KM of 33KV interlinking single run UG Cable(3X400 Sqmm. XLPE)from 33/11KV Yakathpura SS to 33/11KV Panjesha SS in Hyderabad South Division of Hyderabad South Circle in Master Plan SD-III of Masterplan Division-II of Masterplan Hyderabad Circle under T&D Improvement works(Summer Action Plan 2025)
WBS Element :- T-2431-12-02-03-01-001
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 2.5 | Survey line&cabl inc peg mark,tree clear&trail pits | Elect | Labour | SWR22092 | 765 | KM | 1912.5
2 | 9 | Loading of 11KV/33KV XLPE UG Cable Drums for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 9216
3 | 5 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excludingof loading unloading)- Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 16498.5
4 | 9 | Un loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 9216
5 | 1400 | Excavation & laying of UG Cable in Single Run - Laying of Single Run 33KV 3x400sqmm XLPE UG cable including excavation of trench of size 450mm wide1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required , back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc - .depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. - Along the CC / BT multi layer road requiring compressor - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11927 | 1175.56 | M | 1645784
6 | 100 | Excavation & laying of UG Cable in Single Run - Laying of Single Run 33KV 3x400sqmm XLPE UG cable including excavation of trench of size 450mm wide1200mm for 33 KV form road level, providing of DWC/GI pipes whereever required depth is not acquiredas per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required , back filling the trench with earth, levelling and and removing the debris from the site inluding the cost of lead and lift etc - .depth of the trench) LT -0.85 mts, 11 KV-1.05Mtrs & 33 KV - 1.20 mtrs. Across the CC/ BT road crossing multi layer road requiring compressor wih hume pipe (excluding the cost of Hume Pipe) - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11936 | 1319.84 | M | 131984
7 | 1000 | Laying of 33KV XLPE UG cable Single Run of Size in Hard Rock (1.2*0.45x1=0.54cum) | Elect | Labour | SWR11003 | 1287 | RMT | 1287000
9 | 25 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 68625
10 | 9 | Making of 33KV 3X400Sq.mm XLPE UG Cable Straight through joints | Elect | Labour | SWR10382 | 5700.78 | EA | 51307.02
11 | 600 | Supply 6" B Class GI pipe 5mm thck 20Kg/M | Elect | Supply | SMR40081 | 1044 | M | 626400
12 | 500 | supply of 6" DWC pipe | Elect | Supply | SMR11610 | 1012 | M | 506000
13 | 100 | Supply of Hume Pipe Size 9" size | Elect | Supply | SMR40001 | 125 | M | 12500
14 | 6 | Making of 33KV 3X400Sq.mm XLPE UG Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 16588.56
15 | 60 | Raising of Single run 33KV 3x400sqmm UG cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR11954 | 135.66 | M | 8139.6
16 | 2200 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 66000
17 | 25 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters, CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 12100
18 | 1.35 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 298.35
19 | 1.35 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 249.75
20 | 18 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1368
21 | 5.85 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 2410.668
22 | 18 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 900
23 | 12 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 6150.6
24 | 18 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 20376
25 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 5944.08
26 | 3 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting. - Erection of 33 KV DP Structure with 175x85/150x75mm RS joist | Elect | Labour | SWR11276 | 5670 | SET | 17010
27 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properly ramming including transport of materials from road side to location excluding pit excavation - RS Joist 175 x 85 mm | Elect | Labour | SWR10346 | 1934 | EA | 11604
28 | 155 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 6355
29 | 9.54 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 62763.66
30 | 0.186 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 724.098
31 | 0.975 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 3340.35
32 | 3 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | EA | 378
33 | 3 | Un loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | EA | 237
34 | 3 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 13500
35 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 439.89
36 | 3 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 426
37 | 9 | Loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10266 | 41 | EA | 369
38 | 9 | Un loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10584 | 35 | EA | 315
39 | 3 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | SET | 2640
40 | 6 | Supply of CI eath pipe with 80mm dia,2.0 M Length | Elect | Supply | SMR11483 | 2789 | EA | 16734
41 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 7405.2
42 | 6 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 2316
43 | 3 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 159
44 | 30 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 3525
45 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 5568
Total: | [7 empty] | 4662777.826
GST @ 18 % | [7 empty] | 839300.0087
Grand Total: | [7 empty] | 5502077.8347

## T-2431-12-02-03-01-002
SCHEDULE
Name of the Work :- Providing 3rd alternate source of supply to 33/11KV Falaknuma SS from 132/33KV Mailadevarapally EHT SS by laying of 2.5KM of 33KV interlinking double run UG Cable (3X400 Sq.mm. XLPE) from 33/11KV CRPF SS to 33/11KV Falaknuma SS in Hyderabad South Division of Hyderabad South Circle and the work executed by the Master Plan SD-III of Masterplan Division-II in Masterplan Hyderabad Circle under T&D Improvement works (Summer Action Plan-2025)
WBS Element :- T-2431-12-02-03-01-002
Sl No | Estimate Quantity | Description of item | Work Type | Item Short Description | APSS / Month Cl.NumberSSR 11 & 12 | Rate (INR) | UOM | AMOUNT
1 | 2.5 | Survey line&cabl inc peg mark,tree clear&trail pits | Elect | Labour | SWR22092 | 765 | KM | 1912.5
2 | 18 | Loading of 11KV/33KV XLPE UG Cable Drums for all sizes | Elect | Labour | SWR11230 | 1024 | DR | 18432
3 | 9 | Transport of conductor drums, cable drums, fragile material such as kiosks, VCBs,control panels, current transformers, boosters, lightning arrestors, insulators,transformers, meters (which are less in weight and occupy more space) (excludingof loading unloading)- Above 10 Km and upto 20 Km with Lorry for each trip | Elect | Labour | SWR11861 | 3299.7 | EA | 29697.3
4 | 18 | Un loading of 11KV/33KV XLPE UG Cable Drum for all sizes | Elect | Labour | SWR11231 | 1024 | DR | 18432
5 | 900 | Excavation & laying of UG Cable (Double Run) - Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally 4" for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and liftetc - (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs &33 KV - 1.20 mtrs.- Along the CC / BT multi layer road requiring compressor - 33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11980 | 1388.84 | M | 1249956
6 | 100 | Excavation & laying of UG Cable (Double Run) - Laying of XLPE UG cable Double Run including excavation of trench of size 600mm wide1200mm for 33 KV from road level and cable separation with machine cut bricks horizontally 4" for every 3 meters , providing of DWC/GI pipes wherever required depth is not acquired as per the instructions of Engineer in Charge, the prorata basis rates to be adopted for 2 feet, 3feet depths and filling with sand 250mm above the cable and 50mm below the cable, laying of cable, placing 40mm shabad protective slabs, Providing of RFID markers on Shabad Stones wherever required back filling the trench with earth, levelling and removing the debris from the site inluding the cost of lead and liftetc.. (Second cable laying cost not Included) depth of the trench LT-0.85 mts, 11 KV-1.05Mtrs &33 KV - 1.20 mtrs.-.Across the CC/ BT road crossing multi layer road requiring compressor (excluding the cost of Hume pipe)-33 KV 3x400 Sqmm Cable | Elect | Labour | SWR11988 | 1587.07 | M | 158707
7 | 1000 | Laying of 33KV XLPE UG cable Double Run of Size in HardRock (1.2*0.5x1=0.6cum) | Elect | Labour | SWR11002 | 1430 | RMT | 1430000
8 | 500 | Laying of the 33KV cable Double Run along the footpath through by removing & relaying of slabs including material with necessary plastering. - 33KV 3x400sqmm UG Cable | Elect | Labour | SWR11996 | 678.3 |  | 339150
9 | 125 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc-Including the cost of cement | Elect | Labour | SWR10356 | 6579 |  | 822375
10 | 1500 | Laying of 2nd cable in excavated trench | Elect | Labour | SWR10988 | 204.1 | M | 306150
11 | 25 | S&E-Smart RFID marker | Elect | Labour | SWR25089 | 2745 | EA | 68625
12 | 18 | Making of 33KV 3X400Sq.mm XLPE UG Cable Straight through joints | Elect | Labour | SWR10382 | 5700.78 | EA | 102614.04
13 | 1000 | Supply 6" B Class GI pipe 5mm thck 20Kg/M | Elect | Supply | SMR40081 | 1044 | M | 1044000
14 | 500 | supply of 6" DWC pipe | Elect | Supply | SMR11610 | 1012 | M | 506000
15 | 200 | Supply of Hume Pipe Size 9" size | Elect | Supply | SMR40001 | 125 | M | 25000
16 | 12 | Making of 33KV 3X400Sq.mm XLPE UG Cable Outdoor/Indoor End Termination | Elect | Labour | SWR10387 | 2764.76 | EA | 33177.12
17 | 60 | Raising of double run 33KV 3x400sqmm UG cable on already erected support with wooden / MS clamps and connecting it to over head line with cable jumpers including cost of required wooden cleats, lugs and bolts and nuts through GI pipe (excluding the cost of GI pipe) | Elect | Labour | SWR12004 | 323.85 | M | 19431
18 | 2000 | Consultation charges for providing traffic diversions and meeting other exegencies for execution of work during late night hours and wee hours. | Elect | Labour | SWR21903 | 30 | M | 60000
19 | 25 | Supply of RCC cable Joint markers/ Cable route markers of size 700 X 240 X 75 mm duly engraving with 5 mm thick letters, CPDCL 33000/11000 Cable/Cable joint fixing the 300mm below ground level and 400mm above ground level confirming to IS 5820 2001 | Elect | Supply | SMR40085 | 484 | EA | 12100
20 | 1.35 | LOADING of MS Channel,Angles,Flats&Rods | Elect | Labour | SWR10206 | 221 | TO | 298.35
21 | 1.35 | UNLOADING of MS Channel,Angles,Flats&Rod | Elect | Labour | SWR10524 | 185 | TO | 249.75
22 | 18 | Loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10204 | 76 | EA | 1368
23 | 5.85 | Transport of iron materials such as R.S. Joists, Rail Poles, fabricated supports, steel, iron, flat, M.S. Channels etc., by lorries. (excluding of loading & unloading ) Above 10 Km and upto 20 Km | Elect | Labour | SWR10132 | 412.08 | TO | 2410.668
24 | 18 | Un loading of R.S. Joists 175 x 85 mm | Elect | Labour | SWR10522 | 50 | EA | 900
25 | 12 | Fabrication of 175x85/150x75mm RS joist pieces upto 12.5meters length by welding joint together by means of 50x6mm flat and MS channel on either side including the cost of consumable. | Elect | Labour | SWR10642 | 512.55 | EA | 6150.6
26 | 12 | Painting of R.S Joist,Box poles including cross arms and clamps with one coat of red oxid and two coats of Al.paint including cost of paint and consumables | Elect | Labour | SWR10640 | 1132 | EA | 13584
27 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 11 Mtrs PSCC Poles/ Box poles 0.75 M x 0.9 M x 1.95 M | Elect | Labour | SWR11040 | 990.68 | EA | 5944.08
28 | 3 | Assembly and erection of Structure as per specification which includes fixing of top channels and cross bracings, transport of all materials from road side to the location, earthing, back filling with earth ramming etc excluding pit excavation and concreting. - Erection of 33 KV DP Structure with 175x85/150x75mm RS joist | Elect | Labour | SWR11276 | 5670 | SET | 17010
29 | 6 | Erection of pole in position, aligning and setting to work, fixing of cross arms and top clamps, earthing of supports, back filling with earth and stones properlyramming including transport of materials from road side to location excluding pit excavation - Box pole 9/10/11Meter | Elect | Labour | SWR11266 | 2643.83 | EA | 15862.98
30 | 155 | Fabrication and connecting of M.S./ G.I. Flat 50x6mm to risers from earth mat to structures, equipment, marshalling boxes, electrical panels, PLCC panels, fencing posts etc. | Elect | Labour | SWR10919 | 41 | RMT | 6355
31 | 9.54 | Mass concreting of supports erected with CC (1:4:8) using 40 mm, HB G metal including the cost of metal, sand,Cement and curing etc-Including the cost of cement | Elect | Labour | SWR10356 | 6579 | M3 | 62763.66
32 | 0.186 | Coping of 1.5'x1.5'x1 with 1:8 slope Using form boxes(0.031Cumt.) | Elect | Labour | SWR11890 | 3893 | M3 | 724.098
33 | 0.975 | Fabrication of Main and Auxiliary structures with welding usingraw steel such as RS joist, M.S.Angles, Plates, Channels,including the supply and fabrication of 6mm base plate to the RS-Joist poles excluding cost of Mild Steel and transport charges to substation site, including erection. | Elect | Labour | SWR10869 | 3426 | TO | 3340.35
34 | 3 | Loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10239 | 126 | EA | 378
35 | 3 | Un loading of 33KV 800 Amps AB Switch | Elect | Labour | SWR10557 | 79 | EA | 237
36 | 3 | Erection of 33 KV AB Switch including alignment and earthing | Elect | Labour | SWR10392 | 4500 | EA | 13500
37 | 3 | Making of coil earthing pole with 8mm GI wireNut&Bolts for AB Switch | Elect | Labour | SWR12331 | 146.63 | EA | 439.89
38 | 3 | Painting of operating rods of 33kV, 11kV AB switches with post office red colour (including cost of paint) | Elect | Labour | SWR10881 | 142 | EA | 426
39 | 9 | Loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10266 | 41 | EA | 369
40 | 9 | Un loading of 33 KV, 10 KA LAs Station type | Elect | Labour | SWR10584 | 35 | EA | 315
41 | 3 | Erection of 33 KV LAS station/Line type including earthing | Elect | Labour | SWR10396 | 880 | SET | 2640
42 | 6 | Supply of CI eath pipe with 80mm dia,2.0 M Length | Elect | Supply | SMR11483 | 2789 | EA | 16734
43 | 6 | Providing of earthing with excavation of earth pit (0.6 x0.6x2.4 Mts.) duly filling with bentonite, earth , running of earth wire etc., complete, including cost of bentonite and excluding cost of RCC collar of size 0.75M dia x 0.5 M height | Elect | Labour | SWR10357 | 1234.2 | EA | 7405.2
44 | 6 | Providing of RCC Collar guarding to the existing earth pits with damaged masonry including dismantling and removing of existing masonry and fixing the RCC collar of 0.60 M dia X 0.50M height | Elect | Labour | SWR10359 | 386 | EA | 2316
45 | 3 | Painting of feeder name on support including cost of paint | Elect | Labour | SWR12101 | 53 | EA | 159
46 | 30 | Supply of GI Bolts & Nuts etc | Elect | Supply | SMR11488 | 117.5 | KG | 3525
47 | 6 | Excavation of pits in hard rock not requiring blasting. (In hard murram / rock boulders) - 9.1 Mtrs PSCC Poles 0.76 M x 0.76M x 1.83M (2.6" x 2.6" x 6.0") | Elect | Labour | SWR11039 | 928 | EA | 5568
Total: | [7 empty] | 6436732.586
1158611.8655
Grand Total: | [7 empty] | 7595344.4515